## Optimisation Data
Analysis
| 2018 Actual Power Usage: |  | 3633181.008 | kWh
Opt
op1
| Compressor | Control Strategy | Maximum Power | Minimum Power | Maximum Air Output | Minimum Air Output | Average Power | Average Air Output | Total Energy | Total Air Output | Average Efficiency | Time Loaded | Time Loaded | Time Unloaded | Time Unloaded | Loaded Average Power | Loaded Energy | Loaded Energy | Unloaded Energy | Unloaded Energy | Cost of Energy | Loaded Cost | Unloaded Cost | Total Cost | Carbon Used
|  |  | kW | kW | m3/hr | m3/hr | kW | m3/hr | kWh | m3 | kW/m3/hr | hrs | % | hrs | % | kW | kWh | % | kWh | % | £/kWh | £ | £ | £ | Tonnes
| C1 | LoadUnload | 125 | 62 | 947 | 0 | 101.2597 | 587.2868 | 836000 | 4848640 | 0.17242 | 5120 | 62.02% | 3136 | 37.98% | 101.2597 | 836000 | 100% | 0 | 0% | 0.090862 | 75960.8323 | 0 | 75960.8323
| C2 | LoadUnload | 125 | 62 | 947 | 0 | 99.7608 | 564.5753 | 823625 | 4661134 | 0.1767 | 4922 | 59.62% | 3334 | 40.38% | 99.7608 | 823625 | 100% | 0 | 0% | 0.090862 | 74836.4121 | 0 | 74836.4121
| C3 | LoadUnload | 125 | 62 | 947 | 0 | 79.3211 | 254.8733 | 654875 | 2104234 | 0.31122 | 2222 | 26.91% | 6034 | 73.09% | 79.3211 | 654875 | 100% | 0 | 0% | 0.090862 | 59503.4092 | 0 | 59503.4092
| C4 | LoadUnload | 177 | 88 | 1326 | 0 | 130.381 | 627.5051 | 1076425.5 | 5180682 | 0.20778 | 3907 | 47.32% | 4349 | 52.68% | 130.381 | 1076425.5 | 100% | 0 | 0% | 0.090862 | 97806.4317 | 0 | 97806.4317
| C5 | VariableSpeed | 384 | 0 | 2604 | 0 | 41.0386 | 281.061 | 338815 | 2320440 | 0.14601 | 6720 | 81.4% | 1536 | 18.6% | 50.4189 | 338815 | 100% | 0 | 0% | 0.090862 | 30785.4897 | 0 | 30785.4897
| C6 | LoadUnload | 274 | 137 | 1902 | 0 | 198.2816 | 850.7856 | 1637013 | 7024086 | 0.23306 | 3693 | 44.73% | 4563 | 55.27% | 274 | 1011882 | 61.81% | 625131 | 38.19% | 0.090862 | 91941.8648 | 56800.8027 | 148742.6675
| Total |  | 1210 | 411 | 8673 | 0 | 650.0428 | 3166.0872 | 5366753.5 | 26139216 | 0.20531 | 26584 | 53.67% | 22952 | 46.33% | 650.0428 | 4741622.5 | 88.35% | 625131 | 11.65% | 0.090862 | 430834.4399 | 56800.8027 | 487635.2426
op2
| Compressor | Control Strategy | Maximum Power | Minimum Power | Maximum Air Output | Minimum Air Output | Average Power | Average Air Output | Total Energy | Total Air Output | Average Efficiency | Time Loaded | Time Loaded | Time Unloaded | Time Unloaded | Loaded Average Power | Loaded Energy | Loaded Energy | Unloaded Energy | Unloaded Energy | Cost of Energy | Loaded Cost | Unloaded Cost | Total Cost | Carbon Used
|  |  | kW | kW | m3/hr | m3/hr | kW | m3/hr | kWh | m3 | kW/m3/hr | hrs | % | hrs | % | kW | kWh | % | kWh | % | £/kWh | £ | £ | £ | Tonnes
| C1 | OnOff | 125 | 62 | 947 | 0 | 77.5194 | 587.2868 | 640000 | 4848640 | 0.132 | 5120 | 62.02% | 3136 | 37.98% | 125 | 640000 | 100% | 0 | 0% | 0.090862 | 58151.8334 | 0 | 58151.8334
| C2 | OnOff | 125 | 62 | 947 | 0 | 74.5216 | 564.5753 | 615250 | 4661134 | 0.132 | 4922 | 59.62% | 3334 | 40.38% | 125 | 615250 | 100% | 0 | 0% | 0.090862 | 55902.9929 | 0 | 55902.9929
| C3 | OnOff | 125 | 62 | 947 | 0 | 63.0753 | 477.8588 | 520750 | 3945202 | 0.132 | 4166 | 50.46% | 4090 | 49.54% | 125 | 520750 | 100% | 0 | 0% | 0.090862 | 47316.5113 | 0 | 47316.5113
| C4 | OnOff | 177 | 88 | 1326 | 0 | 106.23 | 795.8249 | 877035 | 6570330 | 0.13348 | 4955 | 60.02% | 3301 | 39.98% | 177 | 877035 | 100% | 0 | 0% | 0.090862 | 79689.3643 | 0 | 79689.3643
| C5 | VariableSpeed | 384 | 0 | 2604 | 0 | 84.9763 | 579.0465 | 701564 | 4780608 | 0.14675 | 6755 | 81.82% | 1501 | 18.18% | 103.8585 | 701564 | 100% | 0 | 0% | 0.090862 | 63745.6763 | 0 | 63745.6763
| C6 | OnOff | 274 | 137 | 1902 | 0 | 23.2648 | 161.4949 | 192074 | 1333302 | 0.14406 | 701 | 8.491% | 7555 | 91.51% | 274 | 192074 | 100% | 0 | 0% | 0.090862 | 17452.2738 | 0 | 17452.2738
| Total |  | 1210 | 411 | 8673 | 0 | 429.5873 | 3166.0872 | 3546673 | 26139216 | 0.13568 | 26619 | 53.74% | 22917 | 46.26% | 700.5601 | 3546673 | 100% | 0 | 0% | 0.090862 | 322258.6521 | 0 | 322258.6521
op3
| Compressor | Control Strategy | Maximum Power | Minimum Power | Maximum Air Output | Minimum Air Output | Average Power | Average Air Output | Total Energy | Total Air Output | Average Efficiency | Time Loaded | Time Loaded | Time Unloaded | Time Unloaded | Loaded Average Power | Loaded Energy | Loaded Energy | Unloaded Energy | Unloaded Energy | Cost of Energy | Loaded Cost | Unloaded Cost | Total Cost | Carbon Used
|  |  | kW | kW | m3/hr | m3/hr | kW | m3/hr | kWh | m3 | kW/m3/hr | hrs | % | hrs | % | kW | kWh | % | kWh | % | £/kWh | £ | £ | £ | Tonnes
| C1 | OnOff | 125 | 62 | 947 | 0 | 69.7069 | 528.0993 | 575500 | 4359988 | 0.132 | 4604 | 55.77% | 3652 | 44.23% | 125 | 575500 | 100% | 0 | 0% | 0.090862 | 52291.2189 | 0 | 52291.2189
| C2 | OnOff | 125 | 62 | 947 | 0 | 56.5801 | 428.6506 | 467125 | 3538939 | 0.132 | 3737 | 45.26% | 4519 | 54.74% | 125 | 467125 | 100% | 0 | 0% | 0.090862 | 42444.0237 | 0 | 42444.0237
| C3 | OnOff | 125 | 62 | 947 | 0 | 20.0309 | 151.754 | 165375 | 1252881 | 0.132 | 1323 | 16.02% | 6933 | 83.98% | 125 | 165375 | 100% | 0 | 0% | 0.090862 | 15026.3429 | 0 | 15026.3429
| C4 | OnOff | 177 | 88 | 1326 | 0 | 38.8259 | 290.8656 | 320547 | 2401386 | 0.13348 | 1811 | 21.94% | 6445 | 78.06% | 177 | 320547 | 100% | 0 | 0% | 0.090862 | 29125.6183 | 0 | 29125.6183
| C5 | InletModulation | 384 | 0 | 2604 | 0 | 66.5596 | 1513.7628 | 549516 | 12497626 | 0.04397 | 6742 | 81.66% | 1514 | 18.34% | 81.5064 | 549516 | 100% | 0 | 0% | 0.090862 | 49930.2545 | 0 | 49930.2545
| C6 | OnOff | 274 | 137 | 1902 | 0 | 36.4404 | 252.9549 | 300852 | 2088396 | 0.14406 | 1098 | 13.3% | 7158 | 86.7% | 274 | 300852 | 100% | 0 | 0% | 0.090862 | 27336.0865 | 0 | 27336.0865
| Total |  | 1210 | 411 | 8673 | 0 | 288.1438 | 3166.0872 | 2378915 | 26139216 | 0.091009 | 19315 | 38.99% | 30221 | 61.01% | 549 | 2378915 | 100% | 0 | 0% | 0.090862 | 216153.5448 | 0 | 216153.5448
op4
| Compressor | Control Strategy | Maximum Power | Minimum Power | Maximum Air Output | Minimum Air Output | Average Power | Average Air Output | Total Energy | Total Air Output | Average Efficiency | Time Loaded | Time Loaded | Time Unloaded | Time Unloaded | Loaded Average Power | Loaded Energy | Loaded Energy | Unloaded Energy | Unloaded Energy | Cost of Energy | Loaded Cost | Unloaded Cost | Total Cost | Carbon Used
|  |  | kW | kW | m3/hr | m3/hr | kW | m3/hr | kWh | m3 | kW/m3/hr | hrs | % | hrs | % | kW | kWh | % | kWh | % | £/kWh | £ | £ | £ | Tonnes
| C1 | LoadUnload | 125 | 62 | 947 | 0 | 97.467 | 529.8199 | 804687.5 | 4374193 | 0.18396 | 4619 | 55.95% | 3637 | 44.05% | 97.467 | 804687.5 | 100% | 0 | 0% | 0.090862 | 73115.7085 | 0 | 73115.7085
| C2 | LoadUnload | 125 | 62 | 947 | 0 | 90.9339 | 430.8299 | 750750 | 3556932 | 0.21107 | 3756 | 45.49% | 4500 | 54.51% | 90.9339 | 750750 | 100% | 0 | 0% | 0.090862 | 68214.8264 | 0 | 68214.8264
| C3 | LoadUnload | 125 | 62 | 947 | 0 | 80.169 | 267.7202 | 661875 | 2210298 | 0.29945 | 2334 | 28.27% | 5922 | 71.73% | 80.169 | 661875 | 100% | 0 | 0% | 0.090862 | 60139.4449 | 0 | 60139.4449
| C4 | LoadUnload | 177 | 88 | 1326 | 0 | 119.1148 | 458.7035 | 983412 | 3787056 | 0.25968 | 2856 | 34.59% | 5400 | 65.41% | 119.1148 | 983412 | 100% | 0 | 0% | 0.090862 | 89355.0168 | 0 | 89355.0168
| C5 | InletModulation | 384 | 0 | 2604 | 0 | 65.2557 | 1466.8037 | 538751.2 | 12109931 | 0.044488 | 6766 | 81.95% | 1490 | 18.05% | 79.6262 | 538751.2 | 100% | 0 | 0% | 0.090862 | 48952.1406 | 0 | 48952.1406
| C6 | LoadUnload | 274 | 137 | 1902 | 0 | 137.8795 | 12.21 | 1138333 | 100806 | 11.2923 | 53 | 0.642% | 8203 | 99.36% | 274 | 14522 | 1.276% | 1123811 | 98.72% | 0.090862 | 1319.5014 | 102111.9844 | 103431.4858
| Total |  | 1210 | 411 | 8673 | 0 | 590.8199 | 3166.0872 | 4877808.7 | 26139216 | 0.18661 | 20384 | 41.15% | 29152 | 58.85% | 590.8199 | 3753997.7 | 76.96% | 1123811 | 23.04% | 0.090862 | 341096.6387 | 102111.9844 | 443208.6231

## Optimisation Graphs
Analysis
| 2018 Actual Power Usage: |  | 3633181.008 | kWh
Opt
| LU+VS Data | Units | Compressors | op1 | op2 | op3 | op4 |  |  | Time Loaded | Time Unloaded | Total |  |  | Time Loaded | Time Unloaded | Total |  |  | Loaded Energy | Unloaded Energy | Total |  |  | Loaded Energy | Unloaded Energy | Total |  |  | Loaded Cost | Unloaded Cost | Total
| Average Power | kW | C1 | 101.2597 | 77.5194 | 69.7069 | 97.467 | op1 |  |  |  |  | op1 |  |  |  |  | op1 |  |  |  |  | op1 |  |  |  |  | op1
|  | kW | C2 | 99.7608 | 74.5216 | 56.5801 | 90.9339 |  | C1 | 5120 | 3136 | 8256 |  | C1 | 62.02% | 37.98% | 100% |  | C1 | 836000 | 0 | 836000 |  | C1 | 100% | 0% | 100% |  | C1 | 75960.8323 | 0 | 75960.8323
|  | kW | C3 | 79.3211 | 63.0753 | 20.0309 | 80.169 |  | C2 | 4922 | 3334 | 8256 |  | C2 | 59.62% | 40.38% | 100% |  | C2 | 823625 | 0 | 823625 |  | C2 | 100% | 0% | 100% |  | C2 | 74836.4121 | 0 | 74836.4121
|  | kW | C4 | 130.381 | 106.23 | 38.8259 | 119.1148 |  | C3 | 2222 | 6034 | 8256 |  | C3 | 26.91% | 73.09% | 100% |  | C3 | 654875 | 0 | 654875 |  | C3 | 100% | 0% | 100% |  | C3 | 59503.4092 | 0 | 59503.4092
|  | kW | C5 | 41.0386 | 84.9763 | 66.5596 | 65.2557 |  | C4 | 3907 | 4349 | 8256 |  | C4 | 47.32% | 52.68% | 100% |  | C4 | 1076425.5 | 0 | 1076425.5 |  | C4 | 100% | 0% | 100% |  | C4 | 97806.4317 | 0 | 97806.4317
|  | kW | C6 | 198.2816 | 23.2648 | 36.4404 | 137.8795 |  | C5 | 6720 | 1536 | 8256 |  | C5 | 81.4% | 18.6% | 100% |  | C5 | 338815 | 0 | 338815 |  | C5 | 100% | 0% | 100% |  | C5 | 30785.4897 | 0 | 30785.4897
|  | kW | Total | 650.0428 | 429.5873 | 288.1438 | 590.8199 |  | C6 | 3693 | 4563 | 8256 |  | C6 | 44.73% | 55.27% | 100% |  | C6 | 1011882 | 625131 | 1637013 |  | C6 | 61.81% | 38.19% | 100% |  | C6 | 91941.8648 | 56800.8027 | 148742.6675
| Average Power | % | C1 | 15.58% | 18.05% | 24.19% | 16.5%
|  | % | C2 | 15.35% | 17.35% | 19.64% | 15.39% | op2 |  |  |  |  | op2 |  |  |  |  | op2 |  |  |  |  | op2 |  |  |  |  | op2
|  | % | C3 | 12.2% | 14.68% | 6.952% | 13.57% |  | C1 | 5120 | 3136 | 8256 |  | C1 | 62.02% | 37.98% | 100% |  | C1 | 640000 | 0 | 640000 |  | C1 | 100% | 0% | 100% |  | C1 | 58151.8334 | 0 | 58151.8334
|  | % | C4 | 20.06% | 24.73% | 13.47% | 20.16% |  | C2 | 4922 | 3334 | 8256 |  | C2 | 59.62% | 40.38% | 100% |  | C2 | 615250 | 0 | 615250 |  | C2 | 100% | 0% | 100% |  | C2 | 55902.9929 | 0 | 55902.9929
|  | % | C5 | 6.313% | 19.78% | 23.1% | 11.04% |  | C3 | 4166 | 4090 | 8256 |  | C3 | 50.46% | 49.54% | 100% |  | C3 | 520750 | 0 | 520750 |  | C3 | 100% | 0% | 100% |  | C3 | 47316.5113 | 0 | 47316.5113
|  | % | C6 | 30.5% | 5.416% | 12.65% | 23.34% |  | C4 | 4955 | 3301 | 8256 |  | C4 | 60.02% | 39.98% | 100% |  | C4 | 877035 | 0 | 877035 |  | C4 | 100% | 0% | 100% |  | C4 | 79689.3643 | 0 | 79689.3643
|  | % | Total | 100% | 100% | 100% | 100% |  | C5 | 6755 | 1501 | 8256 |  | C5 | 81.82% | 18.18% | 100% |  | C5 | 701564 | 0 | 701564 |  | C5 | 100% | 0% | 100% |  | C5 | 63745.6763 | 0 | 63745.6763
| Average Air Output | m3/hr | C1 | 587.2868 | 587.2868 | 528.0993 | 529.8199 |  | C6 | 701 | 7555 | 8256 |  | C6 | 8.491% | 91.51% | 100% |  | C6 | 192074 | 0 | 192074 |  | C6 | 100% | 0% | 100% |  | C6 | 17452.2738 | 0 | 17452.2738
|  | m3/hr | C2 | 564.5753 | 564.5753 | 428.6506 | 430.8299
|  | m3/hr | C3 | 254.8733 | 477.8588 | 151.754 | 267.7202 | op3 |  |  |  |  | op3 |  |  |  |  | op3 |  |  |  |  | op3 |  |  |  |  | op3
|  | m3/hr | C4 | 627.5051 | 795.8249 | 290.8656 | 458.7035 |  | C1 | 4604 | 3652 | 8256 |  | C1 | 55.77% | 44.23% | 100% |  | C1 | 575500 | 0 | 575500 |  | C1 | 100% | 0% | 100% |  | C1 | 52291.2189 | 0 | 52291.2189
|  | m3/hr | C5 | 281.061 | 579.0465 | 1513.7628 | 1466.8037 |  | C2 | 3737 | 4519 | 8256 |  | C2 | 45.26% | 54.74% | 100% |  | C2 | 467125 | 0 | 467125 |  | C2 | 100% | 0% | 100% |  | C2 | 42444.0237 | 0 | 42444.0237
|  | m3/hr | C6 | 850.7856 | 161.4949 | 252.9549 | 12.21 |  | C3 | 1323 | 6933 | 8256 |  | C3 | 16.02% | 83.98% | 100% |  | C3 | 165375 | 0 | 165375 |  | C3 | 100% | 0% | 100% |  | C3 | 15026.3429 | 0 | 15026.3429
|  | m3/hr | Total | 3166.0872 | 3166.0872 | 3166.0872 | 3166.0872 |  | C4 | 1811 | 6445 | 8256 |  | C4 | 21.94% | 78.06% | 100% |  | C4 | 320547 | 0 | 320547 |  | C4 | 100% | 0% | 100% |  | C4 | 29125.6183 | 0 | 29125.6183
| Average Air Output | % | C1 | 18.55% | 18.55% | 16.68% | 16.73% |  | C5 | 6742 | 1514 | 8256 |  | C5 | 81.66% | 18.34% | 100% |  | C5 | 549516 | 0 | 549516 |  | C5 | 100% | 0% | 100% |  | C5 | 49930.2545 | 0 | 49930.2545
|  | % | C2 | 17.83% | 17.83% | 13.54% | 13.61% |  | C6 | 1098 | 7158 | 8256 |  | C6 | 13.3% | 86.7% | 100% |  | C6 | 300852 | 0 | 300852 |  | C6 | 100% | 0% | 100% |  | C6 | 27336.0865 | 0 | 27336.0865
|  | % | C3 | 8.05% | 15.09% | 4.793% | 8.456%
|  | % | C4 | 19.82% | 25.14% | 9.187% | 14.49% | op4 |  |  |  |  | op4 |  |  |  |  | op4 |  |  |  |  | op4 |  |  |  |  | op4
|  | % | C5 | 8.877% | 18.29% | 47.81% | 46.33% |  | C1 | 4619 | 3637 | 8256 |  | C1 | 55.95% | 44.05% | 100% |  | C1 | 804687.5 | 0 | 804687.5 |  | C1 | 100% | 0% | 100% |  | C1 | 73115.7085 | 0 | 73115.7085
|  | % | C6 | 26.87% | 5.101% | 7.99% | 0.3857% |  | C2 | 3756 | 4500 | 8256 |  | C2 | 45.49% | 54.51% | 100% |  | C2 | 750750 | 0 | 750750 |  | C2 | 100% | 0% | 100% |  | C2 | 68214.8264 | 0 | 68214.8264
|  | % | Total | 100% | 100% | 100% | 100% |  | C3 | 2334 | 5922 | 8256 |  | C3 | 28.27% | 71.73% | 100% |  | C3 | 661875 | 0 | 661875 |  | C3 | 100% | 0% | 100% |  | C3 | 60139.4449 | 0 | 60139.4449
| Total Energy | kWh | C1 | 836000 | 640000 | 575500 | 804687.5 |  | C4 | 2856 | 5400 | 8256 |  | C4 | 34.59% | 65.41% | 100% |  | C4 | 983412 | 0 | 983412 |  | C4 | 100% | 0% | 100% |  | C4 | 89355.0168 | 0 | 89355.0168
|  | kWh | C2 | 823625 | 615250 | 467125 | 750750 |  | C5 | 6766 | 1490 | 8256 |  | C5 | 81.95% | 18.05% | 100% |  | C5 | 538751.2 | 0 | 538751.2 |  | C5 | 100% | 0% | 100% |  | C5 | 48952.1406 | 0 | 48952.1406
|  | kWh | C3 | 654875 | 520750 | 165375 | 661875 |  | C6 | 53 | 8203 | 8256 |  | C6 | 0.642% | 99.36% | 100% |  | C6 | 14522 | 1123811 | 1138333 |  | C6 | 1.276% | 98.72% | 100% |  | C6 | 1319.5014 | 102111.9844 | 103431.4858
|  | kWh | C4 | 1076425.5 | 877035 | 320547 | 983412
|  | kWh | C5 | 338815 | 701564 | 549516 | 538751.2
|  | kWh | C6 | 1637013 | 192074 | 300852 | 1138333
|  | kWh | Total | 5366753.5 | 3546673 | 2378915 | 4877808.7
| Total Energy | % | C1 | 15.58% | 18.05% | 24.19% | 16.5%
|  | % | C2 | 15.35% | 17.35% | 19.64% | 15.39%
|  | % | C3 | 12.2% | 14.68% | 6.952% | 13.57%
|  | % | C4 | 20.06% | 24.73% | 13.47% | 20.16%
|  | % | C5 | 6.313% | 19.78% | 23.1% | 11.04%
|  | % | C6 | 30.5% | 5.416% | 12.65% | 23.34%
|  | % | Total | 100% | 100% | 100% | 100%
| Total Air Output | m3/hr | C1 | 4848640 | 4848640 | 4359988 | 4374193
|  | m3/hr | C2 | 4661134 | 4661134 | 3538939 | 3556932
|  | m3/hr | C3 | 2104234 | 3945202 | 1252881 | 2210298
|  | m3/hr | C4 | 5180682 | 6570330 | 2401386 | 3787056
|  | m3/hr | C5 | 2320440 | 4780608 | 12497626 | 12109931
|  | m3/hr | C6 | 7024086 | 1333302 | 2088396 | 100806
|  | m3/hr | Total | 26139216 | 26139216 | 26139216 | 26139216
| Total Air Output | % | C1 | 18.55% | 18.55% | 16.68% | 16.73%
|  | % | C2 | 17.83% | 17.83% | 13.54% | 13.61%
|  | % | C3 | 8.05% | 15.09% | 4.793% | 8.456%
|  | % | C4 | 19.82% | 25.14% | 9.187% | 14.49%
|  | % | C5 | 8.877% | 18.29% | 47.81% | 46.33%
|  | % | C6 | 26.87% | 5.101% | 7.99% | 0.3857%
|  | % | Total | 100% | 100% | 100% | 100%
| Average Efficiency | kW/m3/hr | C1 | 0.17242 | 0.132 | 0.132 | 0.18396
|  | kW/m3/hr | C2 | 0.1767 | 0.132 | 0.132 | 0.21107
|  | kW/m3/hr | C3 | 0.31122 | 0.132 | 0.132 | 0.29945
|  | kW/m3/hr | C4 | 0.20778 | 0.13348 | 0.13348 | 0.25968
|  | kW/m3/hr | C5 | 0.14601 | 0.14675 | 0.04397 | 0.044488
|  | kW/m3/hr | C6 | 0.23306 | 0.14406 | 0.14406 | 11.2923
|  | kW/m3/hr | Total | 0.20531 | 0.13568 | 0.091009 | 0.18661
| Time Loaded | hrs | C1 | 5120 | 5120 | 4604 | 4619
|  | hrs | C2 | 4922 | 4922 | 3737 | 3756
|  | hrs | C3 | 2222 | 4166 | 1323 | 2334
|  | hrs | C4 | 3907 | 4955 | 1811 | 2856
|  | hrs | C5 | 6720 | 6755 | 6742 | 6766
|  | hrs | C6 | 3693 | 701 | 1098 | 53
|  | hrs | Total | 26584 | 26619 | 19315 | 20384
| Time Loaded | % | C1 | 62.02% | 62.02% | 55.77% | 55.95%
|  | % | C2 | 59.62% | 59.62% | 45.26% | 45.49%
|  | % | C3 | 26.91% | 50.46% | 16.02% | 28.27%
|  | % | C4 | 47.32% | 60.02% | 21.94% | 34.59%
|  | % | C5 | 81.4% | 81.82% | 81.66% | 81.95%
|  | % | C6 | 44.73% | 8.491% | 13.3% | 0.642%
|  | % | Total | 53.67% | 53.74% | 38.99% | 41.15%
| Time Unloaded | hrs | C1 | 3136 | 3136 | 3652 | 3637
|  | hrs | C2 | 3334 | 3334 | 4519 | 4500
|  | hrs | C3 | 6034 | 4090 | 6933 | 5922
|  | hrs | C4 | 4349 | 3301 | 6445 | 5400
|  | hrs | C5 | 1536 | 1501 | 1514 | 1490
|  | hrs | C6 | 4563 | 7555 | 7158 | 8203
|  | hrs | Total | 22917 | 22917 | 30221 | 29152
| Time Unloaded | % | C1 | 37.98% | 37.98% | 44.23% | 44.05%
|  | % | C2 | 40.38% | 40.38% | 54.74% | 54.51%
|  | % | C3 | 73.09% | 49.54% | 83.98% | 71.73%
|  | % | C4 | 52.68% | 39.98% | 78.06% | 65.41%
|  | % | C5 | 18.6% | 18.18% | 18.34% | 18.05%
|  | % | C6 | 55.27% | 91.51% | 86.7% | 99.36%
|  | % | Total | 46.33% | 46.26% | 61.01% | 58.85%
| Total Time | hrs | C1 | 8256 | 8256 | 8256 | 8256
|  | hrs | C2 | 8256 | 8256 | 8256 | 8256
|  | hrs | C3 | 8256 | 8256 | 8256 | 8256
|  | hrs | C4 | 8256 | 8256 | 8256 | 8256
|  | hrs | C5 | 8256 | 8256 | 8256 | 8256
|  | hrs | C6 | 8256 | 8256 | 8256 | 8256
|  | hrs | Total | 49501 | 49536 | 49536 | 49536
| Loaded Energy | kWh | C1 | 836000 | 640000 | 575500 | 804687.5
|  | kWh | C2 | 823625 | 615250 | 467125 | 750750
|  | kWh | C3 | 654875 | 520750 | 165375 | 661875
|  | kWh | C4 | 1076425.5 | 877035 | 320547 | 983412
|  | kWh | C5 | 338815 | 701564 | 549516 | 538751.2
|  | kWh | C6 | 1011882 | 192074 | 300852 | 14522
|  | kWh | Total | 4741622.5 | 3546673 | 2378915 | 3753997.7
| Loaded Energy | % | C1 | 100% | 100% | 100% | 100%
|  | % | C2 | 100% | 100% | 100% | 100%
|  | % | C3 | 100% | 100% | 100% | 100%
|  | % | C4 | 100% | 100% | 100% | 100%
|  | % | C5 | 100% | 100% | 100% | 100%
|  | % | C6 | 61.81% | 100% | 100% | 1.276%
|  | % | Total | 88.35% | 100% | 100% | 76.96%
| Unloaded Energy | kWh | C1 | 0 | 0 | 0 | 0
|  | kWh | C2 | 0 | 0 | 0 | 0
|  | kWh | C3 | 0 | 0 | 0 | 0
|  | kWh | C4 | 0 | 0 | 0 | 0
|  | kWh | C5 | 0 | 0 | 0 | 0
|  | kWh | C6 | 625131 | 0 | 0 | 1123811
|  | kWh | Total | 625131 | 0 | 0 | 1123811
| Unloaded Energy | % | C1 | 0% | 0% | 0% | 0%
|  | % | C2 | 0% | 0% | 0% | 0%
|  | % | C3 | 0% | 0% | 0% | 0%
|  | % | C4 | 0% | 0% | 0% | 0%
|  | % | C5 | 0% | 0% | 0% | 0%
|  | % | C6 | 38.19% | 0% | 0% | 98.72%
|  | % | Total | 11.65% | 0% | 0% | 23.04%
| Total Energy | kWh | C1 | 836000 | 640000 | 575500 | 804687.5
|  | kWh | C2 | 823625 | 615250 | 467125 | 750750
|  | kWh | C3 | 654875 | 520750 | 165375 | 661875
|  | kWh | C4 | 1076425.5 | 877035 | 320547 | 983412
|  | kWh | C5 | 338815 | 701564 | 549516 | 538751.2
|  | kWh | C6 | 1637013 | 192074 | 300852 | 1138333
|  | kWh | Total | 5366753.5 | 3546673 | 2378915 | 4877808.7
| Loaded Cost | £ | C1 | 75960.8323 | 58151.8334 | 52291.2189 | 73115.7085
|  | £ | C2 | 74836.4121 | 55902.9929 | 42444.0237 | 68214.8264
|  | £ | C3 | 59503.4092 | 47316.5113 | 15026.3429 | 60139.4449
|  | £ | C4 | 97806.4317 | 79689.3643 | 29125.6183 | 89355.0168
|  | £ | C5 | 30785.4897 | 63745.6763 | 49930.2545 | 48952.1406
|  | £ | C6 | 91941.8648 | 17452.2738 | 27336.0865 | 1319.5014
|  | £ | Total | 430834.4399 | 322258.6521 | 216153.5448 | 341096.6387
| Unloaded Cost | £ | C1 | 0 | 0 | 0 | 0
|  | £ | C2 | 0 | 0 | 0 | 0
|  | £ | C3 | 0 | 0 | 0 | 0
|  | £ | C4 | 0 | 0 | 0 | 0
|  | £ | C5 | 0 | 0 | 0 | 0
|  | £ | C6 | 56800.8027 | 0 | 0 | 102111.9844
|  | £ | Total | 56800.8027 | 0 | 0 | 102111.9844
| Total Cost | £ | C1 | 75960.8323 | 58151.8334 | 52291.2189 | 73115.7085
|  | £ | C2 | 74836.4121 | 55902.9929 | 42444.0237 | 68214.8264
|  | £ | C3 | 59503.4092 | 47316.5113 | 15026.3429 | 60139.4449
|  | £ | C4 | 97806.4317 | 79689.3643 | 29125.6183 | 89355.0168
|  | £ | C5 | 30785.4897 | 63745.6763 | 49930.2545 | 48952.1406
|  | £ | C6 | 148742.6675 | 17452.2738 | 27336.0865 | 103431.4858
|  | £ | Total | 487635.2426 | 322258.6521 | 216153.5448 | 443208.6231

## Control Scheme 1 Data
Analysis
| 2018 Actual Power Usage: |  | 3633181.008 | kWh
CS1
op1
| Compressor | Control Strategy | Maximum Power | Minimum Power | Maximum Air Output | Minimum Air Output | Average Power | Average Air Output | Total Energy | Total Air Output | Average Efficiency | Time Loaded | Time Loaded | Time Unloaded | Time Unloaded | Loaded Average Power | Loaded Energy | Loaded Energy | Unloaded Energy | Unloaded Energy | Cost of Energy | Loaded Cost | Unloaded Cost | Total Cost | Carbon Used
|  |  | kW | kW | m3/hr | m3/hr | kW | m3/hr | kWh | m3 | kW/m3/hr | hrs | % | hrs | % | kW | kWh | % | kWh | % | £/kWh | £ | £ | £ | Tonnes
| C1 | LoadUnload | 125 | 62 | 947 | 0 | 101.8956 | 596.922 | 841250 | 4928188 | 0.1707 | 5204 | 63.03% | 3052 | 36.97% | 101.8956 | 841250 | 100% | 0 | 0% | 0.090862 | 76437.8591 | 0 | 76437.8591
| C2 | LoadUnload | 125 | 62 | 947 | 0 | 100.4875 | 575.587 | 829625 | 4752046 | 0.17458 | 5018 | 60.78% | 3238 | 39.22% | 100.4875 | 829625 | 100% | 0 | 0% | 0.090862 | 75381.5856 | 0 | 75381.5856
| C3 | LoadUnload | 125 | 62 | 947 | 0 | 99.3444 | 558.2666 | 820187.5 | 4609049 | 0.17795 | 4867 | 58.95% | 3389 | 41.05% | 99.3444 | 820187.5 | 100% | 0 | 0% | 0.090862 | 74524.0732 | 0 | 74524.0732
| C4 | LoadUnload | 177 | 88 | 1326 | 0 | 104.3863 | 238.0247 | 861813 | 1965132 | 0.43855 | 1482 | 17.95% | 6774 | 82.05% | 104.3863 | 861813 | 100% | 0 | 0% | 0.090862 | 78306.2593 | 0 | 78306.2593
| C5 | VariableSpeed | 384 | 0 | 2604 | 0 | 64.7201 | 438.8829 | 534328.7742 | 3623417 | 0.14747 | 6816 | 82.56% | 1440 | 17.44% | 78.3933 | 534328.7742 | 100% | 0 | 0% | 0.090862 | 48550.3091 | 0 | 48550.3091
| C6 | LoadUnload | 274 | 137 | 1902 | 0 | 191.6274 | 758.4041 | 1582076 | 6261384 | 0.25267 | 3292 | 39.87% | 4964 | 60.13% | 274 | 902008 | 57.01% | 680068 | 42.99% | 0.090862 | 81958.4671 | 61792.5016 | 143750.9687
| Total |  | 1210 | 411 | 8673 | 0 | 662.4613 | 3166.0872 | 5469280.2742 | 26139216 | 0.20924 | 26679 | 53.86% | 22857 | 46.14% | 662.4613 | 4789212.2742 | 87.57% | 680068 | 12.43% | 0.090862 | 435158.5534 | 61792.5016 | 496951.055
op2
| Compressor | Control Strategy | Maximum Power | Minimum Power | Maximum Air Output | Minimum Air Output | Average Power | Average Air Output | Total Energy | Total Air Output | Average Efficiency | Time Loaded | Time Loaded | Time Unloaded | Time Unloaded | Loaded Average Power | Loaded Energy | Loaded Energy | Unloaded Energy | Unloaded Energy | Cost of Energy | Loaded Cost | Unloaded Cost | Total Cost | Carbon Used
|  |  | kW | kW | m3/hr | m3/hr | kW | m3/hr | kWh | m3 | kW/m3/hr | hrs | % | hrs | % | kW | kWh | % | kWh | % | £/kWh | £ | £ | £ | Tonnes
| C1 | OnOff | 125 | 62 | 947 | 0 | 78.7912 | 596.922 | 650500 | 4928188 | 0.132 | 5204 | 63.03% | 3052 | 36.97% | 125 | 650500 | 100% | 0 | 0% | 0.090862 | 59105.8869 | 0 | 59105.8869
| C2 | OnOff | 125 | 62 | 947 | 0 | 75.975 | 575.587 | 627250 | 4752046 | 0.132 | 5018 | 60.78% | 3238 | 39.22% | 125 | 627250 | 100% | 0 | 0% | 0.090862 | 56993.3398 | 0 | 56993.3398
| C3 | OnOff | 125 | 62 | 947 | 0 | 73.6888 | 558.2666 | 608375 | 4609049 | 0.132 | 4867 | 58.95% | 3389 | 41.05% | 125 | 608375 | 100% | 0 | 0% | 0.090862 | 55278.315 | 0 | 55278.315
| C4 | OnOff | 177 | 88 | 1326 | 0 | 31.7725 | 238.0247 | 262314 | 1965132 | 0.13348 | 1482 | 17.95% | 6774 | 82.05% | 177 | 262314 | 100% | 0 | 0% | 0.090862 | 23834.4375 | 0 | 23834.4375
| C5 | VariableSpeed | 384 | 0 | 2604 | 0 | 64.7201 | 438.8829 | 534328.7742 | 3623417 | 0.14747 | 6816 | 82.56% | 1440 | 17.44% | 78.3933 | 534328.7742 | 100% | 0 | 0% | 0.090862 | 48550.3091 | 0 | 48550.3091
| C6 | OnOff | 274 | 137 | 1902 | 0 | 109.2548 | 758.4041 | 902008 | 6261384 | 0.14406 | 3292 | 39.87% | 4964 | 60.13% | 274 | 902008 | 100% | 0 | 0% | 0.090862 | 81958.4671 | 0 | 81958.4671
| Total |  | 1210 | 411 | 8673 | 0 | 434.2025 | 3166.0872 | 3584775.7742 | 26139216 | 0.13714 | 26679 | 53.86% | 22857 | 46.14% | 707.9986 | 3584775.7742 | 100% | 0 | 0% | 0.090862 | 325720.7555 | 0 | 325720.7555
op3
| Compressor | Control Strategy | Maximum Power | Minimum Power | Maximum Air Output | Minimum Air Output | Average Power | Average Air Output | Total Energy | Total Air Output | Average Efficiency | Time Loaded | Time Loaded | Time Unloaded | Time Unloaded | Loaded Average Power | Loaded Energy | Loaded Energy | Unloaded Energy | Unloaded Energy | Cost of Energy | Loaded Cost | Unloaded Cost | Total Cost | Carbon Used
|  |  | kW | kW | m3/hr | m3/hr | kW | m3/hr | kWh | m3 | kW/m3/hr | hrs | % | hrs | % | kW | kWh | % | kWh | % | £/kWh | £ | £ | £ | Tonnes
| C1 | OnOff | 125 | 62 | 947 | 0 | 78.7912 | 596.922 | 650500 | 4928188 | 0.132 | 5204 | 63.03% | 3052 | 36.97% | 125 | 650500 | 100% | 0 | 0% | 0.090862 | 59105.8869 | 0 | 59105.8869
| C2 | OnOff | 125 | 62 | 947 | 0 | 75.975 | 575.587 | 627250 | 4752046 | 0.132 | 5018 | 60.78% | 3238 | 39.22% | 125 | 627250 | 100% | 0 | 0% | 0.090862 | 56993.3398 | 0 | 56993.3398
| C3 | OnOff | 125 | 62 | 947 | 0 | 73.6888 | 558.2666 | 608375 | 4609049 | 0.132 | 4867 | 58.95% | 3389 | 41.05% | 125 | 608375 | 100% | 0 | 0% | 0.090862 | 55278.315 | 0 | 55278.315
| C4 | OnOff | 177 | 88 | 1326 | 0 | 31.7725 | 238.0247 | 262314 | 1965132 | 0.13348 | 1482 | 17.95% | 6774 | 82.05% | 177 | 262314 | 100% | 0 | 0% | 0.090862 | 23834.4375 | 0 | 23834.4375
| C5 | InletModulation | 384 | 0 | 2604 | 0 | 288.216 | 438.8829 | 2379511.4323 | 3623417 | 0.6567 | 8256 | 100% | 0 | 0% | 288.216 | 2379511.4323 | 100% | 0 | 0% | 0.090862 | 216207.738 | 0 | 216207.738
| C6 | OnOff | 274 | 137 | 1902 | 0 | 109.2548 | 758.4041 | 902008 | 6261384 | 0.14406 | 3292 | 39.87% | 4964 | 60.13% | 274 | 902008 | 100% | 0 | 0% | 0.090862 | 81958.4671 | 0 | 81958.4671
| Total |  | 1210 | 411 | 8673 | 0 | 657.6985 | 3166.0872 | 5429958.4323 | 26139216 | 0.20773 | 28119 | 56.76% | 21417 | 43.24% | 891.3591 | 5429958.4323 | 100% | 0 | 0% | 0.090862 | 493378.1844 | 0 | 493378.1844
op4
| Compressor | Control Strategy | Maximum Power | Minimum Power | Maximum Air Output | Minimum Air Output | Average Power | Average Air Output | Total Energy | Total Air Output | Average Efficiency | Time Loaded | Time Loaded | Time Unloaded | Time Unloaded | Loaded Average Power | Loaded Energy | Loaded Energy | Unloaded Energy | Unloaded Energy | Cost of Energy | Loaded Cost | Unloaded Cost | Total Cost | Carbon Used
|  |  | kW | kW | m3/hr | m3/hr | kW | m3/hr | kWh | m3 | kW/m3/hr | hrs | % | hrs | % | kW | kWh | % | kWh | % | £/kWh | £ | £ | £ | Tonnes
| C1 | LoadUnload | 125 | 62 | 947 | 0 | 101.8956 | 596.922 | 841250 | 4928188 | 0.1707 | 5204 | 63.03% | 3052 | 36.97% | 101.8956 | 841250 | 100% | 0 | 0% | 0.090862 | 76437.8591 | 0 | 76437.8591
| C2 | LoadUnload | 125 | 62 | 947 | 0 | 100.4875 | 575.587 | 829625 | 4752046 | 0.17458 | 5018 | 60.78% | 3238 | 39.22% | 100.4875 | 829625 | 100% | 0 | 0% | 0.090862 | 75381.5856 | 0 | 75381.5856
| C3 | LoadUnload | 125 | 62 | 947 | 0 | 99.3444 | 558.2666 | 820187.5 | 4609049 | 0.17795 | 4867 | 58.95% | 3389 | 41.05% | 99.3444 | 820187.5 | 100% | 0 | 0% | 0.090862 | 74524.0732 | 0 | 74524.0732
| C4 | LoadUnload | 177 | 88 | 1326 | 0 | 104.3863 | 238.0247 | 861813 | 1965132 | 0.43855 | 1482 | 17.95% | 6774 | 82.05% | 104.3863 | 861813 | 100% | 0 | 0% | 0.090862 | 78306.2593 | 0 | 78306.2593
| C5 | InletModulation | 384 | 0 | 2604 | 0 | 288.216 | 438.8829 | 2379511.4323 | 3623417 | 0.6567 | 8256 | 100% | 0 | 0% | 288.216 | 2379511.4323 | 100% | 0 | 0% | 0.090862 | 216207.738 | 0 | 216207.738
| C6 | LoadUnload | 274 | 137 | 1902 | 0 | 191.6274 | 758.4041 | 1582076 | 6261384 | 0.25267 | 3292 | 39.87% | 4964 | 60.13% | 274 | 902008 | 57.01% | 680068 | 42.99% | 0.090862 | 81958.4671 | 61792.5016 | 143750.9687
| Total |  | 1210 | 411 | 8673 | 0 | 885.9572 | 3166.0872 | 7314462.9323 | 26139216 | 0.27983 | 28119 | 56.76% | 21417 | 43.24% | 885.9572 | 6634394.9323 | 90.7% | 680068 | 9.298% | 0.090862 | 602815.9823 | 61792.5016 | 664608.4838

## Control Scheme 1 Graphs
Analysis
| 2018 Actual Power Usage: |  | 3633181.008 | kWh
CS1
| LU+VS Data | Units | Compressors | op1 | op2 | op3 | op4 |  |  | Time Loaded | Time Unloaded | Total |  |  | Time Loaded | Time Unloaded | Total |  |  | Loaded Energy | Unloaded Energy | Total |  |  | Loaded Energy | Unloaded Energy | Total |  |  | Loaded Cost | Unloaded Cost | Total
| Average Power | kW | C1 | 101.8956 | 78.7912 | 78.7912 | 101.8956 | op1 |  |  |  |  | op1 |  |  |  |  | op1 |  |  |  |  | op1 |  |  |  |  | op1
|  | kW | C2 | 100.4875 | 75.975 | 75.975 | 100.4875 |  | C1 | 5204 | 3052 | 8256 |  | C1 | 63.03% | 36.97% | 100% |  | C1 | 841250 | 0 | 841250 |  | C1 | 100% | 0% | 100% |  | C1 | 76437.8591 | 0 | 76437.8591
|  | kW | C3 | 99.3444 | 73.6888 | 73.6888 | 99.3444 |  | C2 | 5018 | 3238 | 8256 |  | C2 | 60.78% | 39.22% | 100% |  | C2 | 829625 | 0 | 829625 |  | C2 | 100% | 0% | 100% |  | C2 | 75381.5856 | 0 | 75381.5856
|  | kW | C4 | 104.3863 | 31.7725 | 31.7725 | 104.3863 |  | C3 | 4867 | 3389 | 8256 |  | C3 | 58.95% | 41.05% | 100% |  | C3 | 820187.5 | 0 | 820187.5 |  | C3 | 100% | 0% | 100% |  | C3 | 74524.0732 | 0 | 74524.0732
|  | kW | C5 | 64.7201 | 64.7201 | 288.216 | 288.216 |  | C4 | 1482 | 6774 | 8256 |  | C4 | 17.95% | 82.05% | 100% |  | C4 | 861813 | 0 | 861813 |  | C4 | 100% | 0% | 100% |  | C4 | 78306.2593 | 0 | 78306.2593
|  | kW | C6 | 191.6274 | 109.2548 | 109.2548 | 191.6274 |  | C5 | 6816 | 1440 | 8256 |  | C5 | 82.56% | 17.44% | 100% |  | C5 | 534328.7742 | 0 | 534328.7742 |  | C5 | 100% | 0% | 100% |  | C5 | 48550.3091 | 0 | 48550.3091
|  | kW | Total | 662.4613 | 434.2025 | 657.6985 | 885.9572 |  | C6 | 3292 | 4964 | 8256 |  | C6 | 39.87% | 60.13% | 100% |  | C6 | 902008 | 680068 | 1582076 |  | C6 | 57.01% | 42.99% | 100% |  | C6 | 81958.4671 | 61792.5016 | 143750.9687
| Average Power | % | C1 | 15.38% | 18.15% | 11.98% | 11.5%
|  | % | C2 | 15.17% | 17.5% | 11.55% | 11.34% | op2 |  |  |  |  | op2 |  |  |  |  | op2 |  |  |  |  | op2 |  |  |  |  | op2
|  | % | C3 | 15% | 16.97% | 11.2% | 11.21% |  | C1 | 5204 | 3052 | 8256 |  | C1 | 63.03% | 36.97% | 100% |  | C1 | 650500 | 0 | 650500 |  | C1 | 100% | 0% | 100% |  | C1 | 59105.8869 | 0 | 59105.8869
|  | % | C4 | 15.76% | 7.317% | 4.831% | 11.78% |  | C2 | 5018 | 3238 | 8256 |  | C2 | 60.78% | 39.22% | 100% |  | C2 | 627250 | 0 | 627250 |  | C2 | 100% | 0% | 100% |  | C2 | 56993.3398 | 0 | 56993.3398
|  | % | C5 | 9.77% | 14.91% | 43.82% | 32.53% |  | C3 | 4867 | 3389 | 8256 |  | C3 | 58.95% | 41.05% | 100% |  | C3 | 608375 | 0 | 608375 |  | C3 | 100% | 0% | 100% |  | C3 | 55278.315 | 0 | 55278.315
|  | % | C6 | 28.93% | 25.16% | 16.61% | 21.63% |  | C4 | 1482 | 6774 | 8256 |  | C4 | 17.95% | 82.05% | 100% |  | C4 | 262314 | 0 | 262314 |  | C4 | 100% | 0% | 100% |  | C4 | 23834.4375 | 0 | 23834.4375
|  | % | Total | 100% | 100% | 100% | 100% |  | C5 | 6816 | 1440 | 8256 |  | C5 | 82.56% | 17.44% | 100% |  | C5 | 534328.7742 | 0 | 534328.7742 |  | C5 | 100% | 0% | 100% |  | C5 | 48550.3091 | 0 | 48550.3091
| Average Air Output | m3/hr | C1 | 596.922 | 596.922 | 596.922 | 596.922 |  | C6 | 3292 | 4964 | 8256 |  | C6 | 39.87% | 60.13% | 100% |  | C6 | 902008 | 0 | 902008 |  | C6 | 100% | 0% | 100% |  | C6 | 81958.4671 | 0 | 81958.4671
|  | m3/hr | C2 | 575.587 | 575.587 | 575.587 | 575.587
|  | m3/hr | C3 | 558.2666 | 558.2666 | 558.2666 | 558.2666 | op3 |  |  |  |  | op3 |  |  |  |  | op3 |  |  |  |  | op3 |  |  |  |  | op3
|  | m3/hr | C4 | 238.0247 | 238.0247 | 238.0247 | 238.0247 |  | C1 | 5204 | 3052 | 8256 |  | C1 | 63.03% | 36.97% | 100% |  | C1 | 650500 | 0 | 650500 |  | C1 | 100% | 0% | 100% |  | C1 | 59105.8869 | 0 | 59105.8869
|  | m3/hr | C5 | 438.8829 | 438.8829 | 438.8829 | 438.8829 |  | C2 | 5018 | 3238 | 8256 |  | C2 | 60.78% | 39.22% | 100% |  | C2 | 627250 | 0 | 627250 |  | C2 | 100% | 0% | 100% |  | C2 | 56993.3398 | 0 | 56993.3398
|  | m3/hr | C6 | 758.4041 | 758.4041 | 758.4041 | 758.4041 |  | C3 | 4867 | 3389 | 8256 |  | C3 | 58.95% | 41.05% | 100% |  | C3 | 608375 | 0 | 608375 |  | C3 | 100% | 0% | 100% |  | C3 | 55278.315 | 0 | 55278.315
|  | m3/hr | Total | 3166.0872 | 3166.0872 | 3166.0872 | 3166.0872 |  | C4 | 1482 | 6774 | 8256 |  | C4 | 17.95% | 82.05% | 100% |  | C4 | 262314 | 0 | 262314 |  | C4 | 100% | 0% | 100% |  | C4 | 23834.4375 | 0 | 23834.4375
| Average Air Output | % | C1 | 18.85% | 18.85% | 18.85% | 18.85% |  | C5 | 8256 | 0 | 8256 |  | C5 | 100% | 0% | 100% |  | C5 | 2379511.4323 | 0 | 2379511.4323 |  | C5 | 100% | 0% | 100% |  | C5 | 216207.738 | 0 | 216207.738
|  | % | C2 | 18.18% | 18.18% | 18.18% | 18.18% |  | C6 | 3292 | 4964 | 8256 |  | C6 | 39.87% | 60.13% | 100% |  | C6 | 902008 | 0 | 902008 |  | C6 | 100% | 0% | 100% |  | C6 | 81958.4671 | 0 | 81958.4671
|  | % | C3 | 17.63% | 17.63% | 17.63% | 17.63%
|  | % | C4 | 7.518% | 7.518% | 7.518% | 7.518% | op4 |  |  |  |  | op4 |  |  |  |  | op4 |  |  |  |  | op4 |  |  |  |  | op4
|  | % | C5 | 13.86% | 13.86% | 13.86% | 13.86% |  | C1 | 5204 | 3052 | 8256 |  | C1 | 63.03% | 36.97% | 100% |  | C1 | 841250 | 0 | 841250 |  | C1 | 100% | 0% | 100% |  | C1 | 76437.8591 | 0 | 76437.8591
|  | % | C6 | 23.95% | 23.95% | 23.95% | 23.95% |  | C2 | 5018 | 3238 | 8256 |  | C2 | 60.78% | 39.22% | 100% |  | C2 | 829625 | 0 | 829625 |  | C2 | 100% | 0% | 100% |  | C2 | 75381.5856 | 0 | 75381.5856
|  | % | Total | 100% | 100% | 100% | 100% |  | C3 | 4867 | 3389 | 8256 |  | C3 | 58.95% | 41.05% | 100% |  | C3 | 820187.5 | 0 | 820187.5 |  | C3 | 100% | 0% | 100% |  | C3 | 74524.0732 | 0 | 74524.0732
| Total Energy | kWh | C1 | 841250 | 650500 | 650500 | 841250 |  | C4 | 1482 | 6774 | 8256 |  | C4 | 17.95% | 82.05% | 100% |  | C4 | 861813 | 0 | 861813 |  | C4 | 100% | 0% | 100% |  | C4 | 78306.2593 | 0 | 78306.2593
|  | kWh | C2 | 829625 | 627250 | 627250 | 829625 |  | C5 | 8256 | 0 | 8256 |  | C5 | 100% | 0% | 100% |  | C5 | 2379511.4323 | 0 | 2379511.4323 |  | C5 | 100% | 0% | 100% |  | C5 | 216207.738 | 0 | 216207.738
|  | kWh | C3 | 820187.5 | 608375 | 608375 | 820187.5 |  | C6 | 3292 | 4964 | 8256 |  | C6 | 39.87% | 60.13% | 100% |  | C6 | 902008 | 680068 | 1582076 |  | C6 | 57.01% | 42.99% | 100% |  | C6 | 81958.4671 | 61792.5016 | 143750.9687
|  | kWh | C4 | 861813 | 262314 | 262314 | 861813
|  | kWh | C5 | 534328.7742 | 534328.7742 | 2379511.4323 | 2379511.4323
|  | kWh | C6 | 1582076 | 902008 | 902008 | 1582076
|  | kWh | Total | 5469280.2742 | 3584775.7742 | 5429958.4323 | 7314462.9323
| Total Energy | % | C1 | 15.38% | 18.15% | 11.98% | 11.5%
|  | % | C2 | 15.17% | 17.5% | 11.55% | 11.34%
|  | % | C3 | 15% | 16.97% | 11.2% | 11.21%
|  | % | C4 | 15.76% | 7.317% | 4.831% | 11.78%
|  | % | C5 | 9.77% | 14.91% | 43.82% | 32.53%
|  | % | C6 | 28.93% | 25.16% | 16.61% | 21.63%
|  | % | Total | 100% | 100% | 100% | 100%
| Total Air Output | m3/hr | C1 | 4928188 | 4928188 | 4928188 | 4928188
|  | m3/hr | C2 | 4752046 | 4752046 | 4752046 | 4752046
|  | m3/hr | C3 | 4609049 | 4609049 | 4609049 | 4609049
|  | m3/hr | C4 | 1965132 | 1965132 | 1965132 | 1965132
|  | m3/hr | C5 | 3623417 | 3623417 | 3623417 | 3623417
|  | m3/hr | C6 | 6261384 | 6261384 | 6261384 | 6261384
|  | m3/hr | Total | 26139216 | 26139216 | 26139216 | 26139216
| Total Air Output | % | C1 | 18.85% | 18.85% | 18.85% | 18.85%
|  | % | C2 | 18.18% | 18.18% | 18.18% | 18.18%
|  | % | C3 | 17.63% | 17.63% | 17.63% | 17.63%
|  | % | C4 | 7.518% | 7.518% | 7.518% | 7.518%
|  | % | C5 | 13.86% | 13.86% | 13.86% | 13.86%
|  | % | C6 | 23.95% | 23.95% | 23.95% | 23.95%
|  | % | Total | 100% | 100% | 100% | 100%
| Average Efficiency | kW/m3/hr | C1 | 0.1707 | 0.132 | 0.132 | 0.1707
|  | kW/m3/hr | C2 | 0.17458 | 0.132 | 0.132 | 0.17458
|  | kW/m3/hr | C3 | 0.17795 | 0.132 | 0.132 | 0.17795
|  | kW/m3/hr | C4 | 0.43855 | 0.13348 | 0.13348 | 0.43855
|  | kW/m3/hr | C5 | 0.14747 | 0.14747 | 0.6567 | 0.6567
|  | kW/m3/hr | C6 | 0.25267 | 0.14406 | 0.14406 | 0.25267
|  | kW/m3/hr | Total | 0.20924 | 0.13714 | 0.20773 | 0.27983
| Time Loaded | hrs | C1 | 5204 | 5204 | 5204 | 5204
|  | hrs | C2 | 5018 | 5018 | 5018 | 5018
|  | hrs | C3 | 4867 | 4867 | 4867 | 4867
|  | hrs | C4 | 1482 | 1482 | 1482 | 1482
|  | hrs | C5 | 6816 | 6816 | 8256 | 8256
|  | hrs | C6 | 3292 | 3292 | 3292 | 3292
|  | hrs | Total | 26679 | 26679 | 28119 | 28119
| Time Loaded | % | C1 | 63.03% | 63.03% | 63.03% | 63.03%
|  | % | C2 | 60.78% | 60.78% | 60.78% | 60.78%
|  | % | C3 | 58.95% | 58.95% | 58.95% | 58.95%
|  | % | C4 | 17.95% | 17.95% | 17.95% | 17.95%
|  | % | C5 | 82.56% | 82.56% | 100% | 100%
|  | % | C6 | 39.87% | 39.87% | 39.87% | 39.87%
|  | % | Total | 53.86% | 53.86% | 56.76% | 56.76%
| Time Unloaded | hrs | C1 | 3052 | 3052 | 3052 | 3052
|  | hrs | C2 | 3238 | 3238 | 3238 | 3238
|  | hrs | C3 | 3389 | 3389 | 3389 | 3389
|  | hrs | C4 | 6774 | 6774 | 6774 | 6774
|  | hrs | C5 | 1440 | 1440 | 0 | 0
|  | hrs | C6 | 4964 | 4964 | 4964 | 4964
|  | hrs | Total | 22857 | 22857 | 21417 | 21417
| Time Unloaded | % | C1 | 36.97% | 36.97% | 36.97% | 36.97%
|  | % | C2 | 39.22% | 39.22% | 39.22% | 39.22%
|  | % | C3 | 41.05% | 41.05% | 41.05% | 41.05%
|  | % | C4 | 82.05% | 82.05% | 82.05% | 82.05%
|  | % | C5 | 17.44% | 17.44% | 0% | 0%
|  | % | C6 | 60.13% | 60.13% | 60.13% | 60.13%
|  | % | Total | 46.14% | 46.14% | 43.24% | 43.24%
| Total Time | hrs | C1 | 8256 | 8256 | 8256 | 8256
|  | hrs | C2 | 8256 | 8256 | 8256 | 8256
|  | hrs | C3 | 8256 | 8256 | 8256 | 8256
|  | hrs | C4 | 8256 | 8256 | 8256 | 8256
|  | hrs | C5 | 8256 | 8256 | 8256 | 8256
|  | hrs | C6 | 8256 | 8256 | 8256 | 8256
|  | hrs | Total | 49536 | 49536 | 49536 | 49536
| Loaded Energy | kWh | C1 | 841250 | 650500 | 650500 | 841250
|  | kWh | C2 | 829625 | 627250 | 627250 | 829625
|  | kWh | C3 | 820187.5 | 608375 | 608375 | 820187.5
|  | kWh | C4 | 861813 | 262314 | 262314 | 861813
|  | kWh | C5 | 534328.7742 | 534328.7742 | 2379511.4323 | 2379511.4323
|  | kWh | C6 | 902008 | 902008 | 902008 | 902008
|  | kWh | Total | 4789212.2742 | 3584775.7742 | 5429958.4323 | 6634394.9323
| Loaded Energy | % | C1 | 100% | 100% | 100% | 100%
|  | % | C2 | 100% | 100% | 100% | 100%
|  | % | C3 | 100% | 100% | 100% | 100%
|  | % | C4 | 100% | 100% | 100% | 100%
|  | % | C5 | 100% | 100% | 100% | 100%
|  | % | C6 | 57.01% | 100% | 100% | 57.01%
|  | % | Total | 87.57% | 100% | 100% | 90.7%
| Unloaded Energy | kWh | C1 | 0 | 0 | 0 | 0
|  | kWh | C2 | 0 | 0 | 0 | 0
|  | kWh | C3 | 0 | 0 | 0 | 0
|  | kWh | C4 | 0 | 0 | 0 | 0
|  | kWh | C5 | 0 | 0 | 0 | 0
|  | kWh | C6 | 680068 | 0 | 0 | 680068
|  | kWh | Total | 680068 | 0 | 0 | 680068
| Unloaded Energy | % | C1 | 0% | 0% | 0% | 0%
|  | % | C2 | 0% | 0% | 0% | 0%
|  | % | C3 | 0% | 0% | 0% | 0%
|  | % | C4 | 0% | 0% | 0% | 0%
|  | % | C5 | 0% | 0% | 0% | 0%
|  | % | C6 | 42.99% | 0% | 0% | 42.99%
|  | % | Total | 12.43% | 0% | 0% | 9.298%
| Total Energy | kWh | C1 | 841250 | 650500 | 650500 | 841250
|  | kWh | C2 | 829625 | 627250 | 627250 | 829625
|  | kWh | C3 | 820187.5 | 608375 | 608375 | 820187.5
|  | kWh | C4 | 861813 | 262314 | 262314 | 861813
|  | kWh | C5 | 534328.7742 | 534328.7742 | 2379511.4323 | 2379511.4323
|  | kWh | C6 | 1582076 | 902008 | 902008 | 1582076
|  | kWh | Total | 5469280.2742 | 3584775.7742 | 5429958.4323 | 7314462.9323
| Loaded Cost | £ | C1 | 76437.8591 | 59105.8869 | 59105.8869 | 76437.8591
|  | £ | C2 | 75381.5856 | 56993.3398 | 56993.3398 | 75381.5856
|  | £ | C3 | 74524.0732 | 55278.315 | 55278.315 | 74524.0732
|  | £ | C4 | 78306.2593 | 23834.4375 | 23834.4375 | 78306.2593
|  | £ | C5 | 48550.3091 | 48550.3091 | 216207.738 | 216207.738
|  | £ | C6 | 81958.4671 | 81958.4671 | 81958.4671 | 81958.4671
|  | £ | Total | 435158.5534 | 325720.7555 | 493378.1844 | 602815.9823
| Unloaded Cost | £ | C1 | 0 | 0 | 0 | 0
|  | £ | C2 | 0 | 0 | 0 | 0
|  | £ | C3 | 0 | 0 | 0 | 0
|  | £ | C4 | 0 | 0 | 0 | 0
|  | £ | C5 | 0 | 0 | 0 | 0
|  | £ | C6 | 61792.5016 | 0 | 0 | 61792.5016
|  | £ | Total | 61792.5016 | 0 | 0 | 61792.5016
| Total Cost | £ | C1 | 76437.8591 | 59105.8869 | 59105.8869 | 76437.8591
|  | £ | C2 | 75381.5856 | 56993.3398 | 56993.3398 | 75381.5856
|  | £ | C3 | 74524.0732 | 55278.315 | 55278.315 | 74524.0732
|  | £ | C4 | 78306.2593 | 23834.4375 | 23834.4375 | 78306.2593
|  | £ | C5 | 48550.3091 | 48550.3091 | 216207.738 | 216207.738
|  | £ | C6 | 143750.9687 | 81958.4671 | 81958.4671 | 143750.9687
|  | £ | Total | 496951.055 | 325720.7555 | 493378.1844 | 664608.4838

## Control Scheme 2 Data
Analysis
| 2018 Actual Power Usage: |  | 3633181.008 | kWh
CS2
op1
| Compressor | Control Strategy | Maximum Power | Minimum Power | Maximum Air Output | Minimum Air Output | Average Power | Average Air Output | Total Energy | Total Air Output | Average Efficiency | Time Loaded | Time Loaded | Time Unloaded | Time Unloaded | Loaded Average Power | Loaded Energy | Loaded Energy | Unloaded Energy | Unloaded Energy | Cost of Energy | Loaded Cost | Unloaded Cost | Total Cost | Carbon Used
|  |  | kW | kW | m3/hr | m3/hr | kW | m3/hr | kWh | m3 | kW/m3/hr | hrs | % | hrs | % | kW | kWh | % | kWh | % | £/kWh | £ | £ | £ | Tonnes
| C1 | LoadUnload | 125 | 62 | 947 | 0 | 101.2597 | 587.2868 | 836000 | 4848640 | 0.17242 | 5120 | 62.02% | 3136 | 37.98% | 101.2597 | 836000 | 100% | 0 | 0% | 0.090862 | 75960.8323 | 0 | 75960.8323
| C2 | LoadUnload | 125 | 62 | 947 | 0 | 99.7608 | 564.5753 | 823625 | 4661134 | 0.1767 | 4922 | 59.62% | 3334 | 40.38% | 99.7608 | 823625 | 100% | 0 | 0% | 0.090862 | 74836.4121 | 0 | 74836.4121
| C3 | LoadUnload | 125 | 62 | 947 | 0 | 94.0452 | 477.9735 | 776437.5 | 3946149 | 0.19676 | 4167 | 50.47% | 4089 | 49.53% | 94.0452 | 776437.5 | 100% | 0 | 0% | 0.090862 | 70548.8502 | 0 | 70548.8502
| C4 | LoadUnload | 177 | 88 | 1326 | 0 | 141.5936 | 795.5036 | 1168996.5 | 6567678 | 0.17799 | 4953 | 59.99% | 3303 | 40.01% | 141.5936 | 1168996.5 | 100% | 0 | 0% | 0.090862 | 106217.6401 | 0 | 106217.6401
| C5 | VariableSpeed | 384 | 0 | 2604 | 0 | 85.4198 | 579.253 | 705225.8802 | 4782313 | 0.14747 | 6816 | 82.56% | 1440 | 17.44% | 103.4662 | 705225.8802 | 100% | 0 | 0% | 0.090862 | 64078.4029 | 0 | 64078.4029
| C6 | LoadUnload | 274 | 137 | 1902 | 0 | 148.6324 | 161.4949 | 1227109 | 1333302 | 0.92035 | 701 | 8.491% | 7555 | 91.51% | 274 | 192074 | 15.65% | 1035035 | 84.35% | 0.090862 | 17452.2738 | 94045.5982 | 111497.872
| Total |  | 1210 | 411 | 8673 | 0 | 670.7115 | 3166.0872 | 5537393.8802 | 26139216 | 0.21184 | 26679 | 53.86% | 22857 | 46.14% | 670.7115 | 4502358.8802 | 81.31% | 1035035 | 18.69% | 0.090862 | 409094.4116 | 94045.5982 | 503140.0098
op2
| Compressor | Control Strategy | Maximum Power | Minimum Power | Maximum Air Output | Minimum Air Output | Average Power | Average Air Output | Total Energy | Total Air Output | Average Efficiency | Time Loaded | Time Loaded | Time Unloaded | Time Unloaded | Loaded Average Power | Loaded Energy | Loaded Energy | Unloaded Energy | Unloaded Energy | Cost of Energy | Loaded Cost | Unloaded Cost | Total Cost | Carbon Used
|  |  | kW | kW | m3/hr | m3/hr | kW | m3/hr | kWh | m3 | kW/m3/hr | hrs | % | hrs | % | kW | kWh | % | kWh | % | £/kWh | £ | £ | £ | Tonnes
| C1 | OnOff | 125 | 62 | 947 | 0 | 77.5194 | 587.2868 | 640000 | 4848640 | 0.132 | 5120 | 62.02% | 3136 | 37.98% | 125 | 640000 | 100% | 0 | 0% | 0.090862 | 58151.8334 | 0 | 58151.8334
| C2 | OnOff | 125 | 62 | 947 | 0 | 74.5216 | 564.5753 | 615250 | 4661134 | 0.132 | 4922 | 59.62% | 3334 | 40.38% | 125 | 615250 | 100% | 0 | 0% | 0.090862 | 55902.9929 | 0 | 55902.9929
| C3 | OnOff | 125 | 62 | 947 | 0 | 63.0905 | 477.9735 | 520875 | 3946149 | 0.132 | 4167 | 50.47% | 4089 | 49.53% | 125 | 520875 | 100% | 0 | 0% | 0.090862 | 47327.8691 | 0 | 47327.8691
| C4 | OnOff | 177 | 88 | 1326 | 0 | 106.1871 | 795.5036 | 876681 | 6567678 | 0.13348 | 4953 | 59.99% | 3303 | 40.01% | 177 | 876681 | 100% | 0 | 0% | 0.090862 | 79657.1991 | 0 | 79657.1991
| C5 | VariableSpeed | 384 | 0 | 2604 | 0 | 85.4198 | 579.253 | 705225.8802 | 4782313 | 0.14747 | 6816 | 82.56% | 1440 | 17.44% | 103.4662 | 705225.8802 | 100% | 0 | 0% | 0.090862 | 64078.4029 | 0 | 64078.4029
| C6 | OnOff | 274 | 137 | 1902 | 0 | 23.2648 | 161.4949 | 192074 | 1333302 | 0.14406 | 701 | 8.491% | 7555 | 91.51% | 274 | 192074 | 100% | 0 | 0% | 0.090862 | 17452.2738 | 0 | 17452.2738
| Total |  | 1210 | 411 | 8673 | 0 | 430.0031 | 3166.0872 | 3550105.8802 | 26139216 | 0.13582 | 26679 | 53.86% | 22857 | 46.14% | 700.9421 | 3550105.8802 | 100% | 0 | 0% | 0.090862 | 322570.5713 | 0 | 322570.5713
op3
| Compressor | Control Strategy | Maximum Power | Minimum Power | Maximum Air Output | Minimum Air Output | Average Power | Average Air Output | Total Energy | Total Air Output | Average Efficiency | Time Loaded | Time Loaded | Time Unloaded | Time Unloaded | Loaded Average Power | Loaded Energy | Loaded Energy | Unloaded Energy | Unloaded Energy | Cost of Energy | Loaded Cost | Unloaded Cost | Total Cost | Carbon Used
|  |  | kW | kW | m3/hr | m3/hr | kW | m3/hr | kWh | m3 | kW/m3/hr | hrs | % | hrs | % | kW | kWh | % | kWh | % | £/kWh | £ | £ | £ | Tonnes
| C1 | OnOff | 125 | 62 | 947 | 0 | 77.5194 | 587.2868 | 640000 | 4848640 | 0.132 | 5120 | 62.02% | 3136 | 37.98% | 125 | 640000 | 100% | 0 | 0% | 0.090862 | 58151.8334 | 0 | 58151.8334
| C2 | OnOff | 125 | 62 | 947 | 0 | 74.5216 | 564.5753 | 615250 | 4661134 | 0.132 | 4922 | 59.62% | 3334 | 40.38% | 125 | 615250 | 100% | 0 | 0% | 0.090862 | 55902.9929 | 0 | 55902.9929
| C3 | OnOff | 125 | 62 | 947 | 0 | 63.0905 | 477.9735 | 520875 | 3946149 | 0.132 | 4167 | 50.47% | 4089 | 49.53% | 125 | 520875 | 100% | 0 | 0% | 0.090862 | 47327.8691 | 0 | 47327.8691
| C4 | OnOff | 177 | 88 | 1326 | 0 | 106.1871 | 795.5036 | 876681 | 6567678 | 0.13348 | 4953 | 59.99% | 3303 | 40.01% | 177 | 876681 | 100% | 0 | 0% | 0.090862 | 79657.1991 | 0 | 79657.1991
| C5 | InletModulation | 384 | 0 | 2604 | 0 | 294.4259 | 579.253 | 2430780.5641 | 4782313 | 0.50829 | 8256 | 100% | 0 | 0% | 294.4259 | 2430780.5641 | 100% | 0 | 0% | 0.090862 | 220866.1661 | 0 | 220866.1661
| C6 | OnOff | 274 | 137 | 1902 | 0 | 23.2648 | 161.4949 | 192074 | 1333302 | 0.14406 | 701 | 8.491% | 7555 | 91.51% | 274 | 192074 | 100% | 0 | 0% | 0.090862 | 17452.2738 | 0 | 17452.2738
| Total |  | 1210 | 411 | 8673 | 0 | 639.0093 | 3166.0872 | 5275660.5641 | 26139216 | 0.20183 | 28119 | 56.76% | 21417 | 43.24% | 860.9281 | 5275660.5641 | 100% | 0 | 0% | 0.090862 | 479358.3345 | 0 | 479358.3345
op4
| Compressor | Control Strategy | Maximum Power | Minimum Power | Maximum Air Output | Minimum Air Output | Average Power | Average Air Output | Total Energy | Total Air Output | Average Efficiency | Time Loaded | Time Loaded | Time Unloaded | Time Unloaded | Loaded Average Power | Loaded Energy | Loaded Energy | Unloaded Energy | Unloaded Energy | Cost of Energy | Loaded Cost | Unloaded Cost | Total Cost | Carbon Used
|  |  | kW | kW | m3/hr | m3/hr | kW | m3/hr | kWh | m3 | kW/m3/hr | hrs | % | hrs | % | kW | kWh | % | kWh | % | £/kWh | £ | £ | £ | Tonnes
| C1 | LoadUnload | 125 | 62 | 947 | 0 | 101.2597 | 587.2868 | 836000 | 4848640 | 0.17242 | 5120 | 62.02% | 3136 | 37.98% | 101.2597 | 836000 | 100% | 0 | 0% | 0.090862 | 75960.8323 | 0 | 75960.8323
| C2 | LoadUnload | 125 | 62 | 947 | 0 | 99.7608 | 564.5753 | 823625 | 4661134 | 0.1767 | 4922 | 59.62% | 3334 | 40.38% | 99.7608 | 823625 | 100% | 0 | 0% | 0.090862 | 74836.4121 | 0 | 74836.4121
| C3 | LoadUnload | 125 | 62 | 947 | 0 | 94.0452 | 477.9735 | 776437.5 | 3946149 | 0.19676 | 4167 | 50.47% | 4089 | 49.53% | 94.0452 | 776437.5 | 100% | 0 | 0% | 0.090862 | 70548.8502 | 0 | 70548.8502
| C4 | LoadUnload | 177 | 88 | 1326 | 0 | 141.5936 | 795.5036 | 1168996.5 | 6567678 | 0.17799 | 4953 | 59.99% | 3303 | 40.01% | 141.5936 | 1168996.5 | 100% | 0 | 0% | 0.090862 | 106217.6401 | 0 | 106217.6401
| C5 | InletModulation | 384 | 0 | 2604 | 0 | 294.4259 | 579.253 | 2430780.5641 | 4782313 | 0.50829 | 8256 | 100% | 0 | 0% | 294.4259 | 2430780.5641 | 100% | 0 | 0% | 0.090862 | 220866.1661 | 0 | 220866.1661
| C6 | LoadUnload | 274 | 137 | 1902 | 0 | 148.6324 | 161.4949 | 1227109 | 1333302 | 0.92035 | 701 | 8.491% | 7555 | 91.51% | 274 | 192074 | 15.65% | 1035035 | 84.35% | 0.090862 | 17452.2738 | 94045.5982 | 111497.872
| Total |  | 1210 | 411 | 8673 | 0 | 879.7176 | 3166.0872 | 7262948.5641 | 26139216 | 0.27786 | 28119 | 56.76% | 21417 | 43.24% | 879.7176 | 6227913.5641 | 85.75% | 1035035 | 14.25% | 0.090862 | 565882.1748 | 94045.5982 | 659927.773

## Control Scheme 2 Graphs
Analysis
| 2018 Actual Power Usage: |  | 3633181.008 | kWh
CS2
| LU+VS Data | Units | Compressors | op1 | op2 | op3 | op4 |  |  | Time Loaded | Time Unloaded | Total |  |  | Time Loaded | Time Unloaded | Total |  |  | Loaded Energy | Unloaded Energy | Total |  |  | Loaded Energy | Unloaded Energy | Total |  |  | Loaded Cost | Unloaded Cost | Total
| Average Power | kW | C1 | 101.2597 | 77.5194 | 77.5194 | 101.2597 | op1 |  |  |  |  | op1 |  |  |  |  | op1 |  |  |  |  | op1 |  |  |  |  | op1
|  | kW | C2 | 99.7608 | 74.5216 | 74.5216 | 99.7608 |  | C1 | 5120 | 3136 | 8256 |  | C1 | 62.02% | 37.98% | 100% |  | C1 | 836000 | 0 | 836000 |  | C1 | 100% | 0% | 100% |  | C1 | 75960.8323 | 0 | 75960.8323
|  | kW | C3 | 94.0452 | 63.0905 | 63.0905 | 94.0452 |  | C2 | 4922 | 3334 | 8256 |  | C2 | 59.62% | 40.38% | 100% |  | C2 | 823625 | 0 | 823625 |  | C2 | 100% | 0% | 100% |  | C2 | 74836.4121 | 0 | 74836.4121
|  | kW | C4 | 141.5936 | 106.1871 | 106.1871 | 141.5936 |  | C3 | 4167 | 4089 | 8256 |  | C3 | 50.47% | 49.53% | 100% |  | C3 | 776437.5 | 0 | 776437.5 |  | C3 | 100% | 0% | 100% |  | C3 | 70548.8502 | 0 | 70548.8502
|  | kW | C5 | 85.4198 | 85.4198 | 294.4259 | 294.4259 |  | C4 | 4953 | 3303 | 8256 |  | C4 | 59.99% | 40.01% | 100% |  | C4 | 1168996.5 | 0 | 1168996.5 |  | C4 | 100% | 0% | 100% |  | C4 | 106217.6401 | 0 | 106217.6401
|  | kW | C6 | 148.6324 | 23.2648 | 23.2648 | 148.6324 |  | C5 | 6816 | 1440 | 8256 |  | C5 | 82.56% | 17.44% | 100% |  | C5 | 705225.8802 | 0 | 705225.8802 |  | C5 | 100% | 0% | 100% |  | C5 | 64078.4029 | 0 | 64078.4029
|  | kW | Total | 670.7115 | 430.0031 | 639.0093 | 879.7176 |  | C6 | 701 | 7555 | 8256 |  | C6 | 8.491% | 91.51% | 100% |  | C6 | 192074 | 1035035 | 1227109 |  | C6 | 15.65% | 84.35% | 100% |  | C6 | 17452.2738 | 94045.5982 | 111497.872
| Average Power | % | C1 | 15.1% | 18.03% | 12.13% | 11.51%
|  | % | C2 | 14.87% | 17.33% | 11.66% | 11.34% | op2 |  |  |  |  | op2 |  |  |  |  | op2 |  |  |  |  | op2 |  |  |  |  | op2
|  | % | C3 | 14.02% | 14.67% | 9.873% | 10.69% |  | C1 | 5120 | 3136 | 8256 |  | C1 | 62.02% | 37.98% | 100% |  | C1 | 640000 | 0 | 640000 |  | C1 | 100% | 0% | 100% |  | C1 | 58151.8334 | 0 | 58151.8334
|  | % | C4 | 21.11% | 24.69% | 16.62% | 16.1% |  | C2 | 4922 | 3334 | 8256 |  | C2 | 59.62% | 40.38% | 100% |  | C2 | 615250 | 0 | 615250 |  | C2 | 100% | 0% | 100% |  | C2 | 55902.9929 | 0 | 55902.9929
|  | % | C5 | 12.74% | 19.86% | 46.08% | 33.47% |  | C3 | 4167 | 4089 | 8256 |  | C3 | 50.47% | 49.53% | 100% |  | C3 | 520875 | 0 | 520875 |  | C3 | 100% | 0% | 100% |  | C3 | 47327.8691 | 0 | 47327.8691
|  | % | C6 | 22.16% | 5.41% | 3.641% | 16.9% |  | C4 | 4953 | 3303 | 8256 |  | C4 | 59.99% | 40.01% | 100% |  | C4 | 876681 | 0 | 876681 |  | C4 | 100% | 0% | 100% |  | C4 | 79657.1991 | 0 | 79657.1991
|  | % | Total | 100% | 100% | 100% | 100% |  | C5 | 6816 | 1440 | 8256 |  | C5 | 82.56% | 17.44% | 100% |  | C5 | 705225.8802 | 0 | 705225.8802 |  | C5 | 100% | 0% | 100% |  | C5 | 64078.4029 | 0 | 64078.4029
| Average Air Output | m3/hr | C1 | 587.2868 | 587.2868 | 587.2868 | 587.2868 |  | C6 | 701 | 7555 | 8256 |  | C6 | 8.491% | 91.51% | 100% |  | C6 | 192074 | 0 | 192074 |  | C6 | 100% | 0% | 100% |  | C6 | 17452.2738 | 0 | 17452.2738
|  | m3/hr | C2 | 564.5753 | 564.5753 | 564.5753 | 564.5753
|  | m3/hr | C3 | 477.9735 | 477.9735 | 477.9735 | 477.9735 | op3 |  |  |  |  | op3 |  |  |  |  | op3 |  |  |  |  | op3 |  |  |  |  | op3
|  | m3/hr | C4 | 795.5036 | 795.5036 | 795.5036 | 795.5036 |  | C1 | 5120 | 3136 | 8256 |  | C1 | 62.02% | 37.98% | 100% |  | C1 | 640000 | 0 | 640000 |  | C1 | 100% | 0% | 100% |  | C1 | 58151.8334 | 0 | 58151.8334
|  | m3/hr | C5 | 579.253 | 579.253 | 579.253 | 579.253 |  | C2 | 4922 | 3334 | 8256 |  | C2 | 59.62% | 40.38% | 100% |  | C2 | 615250 | 0 | 615250 |  | C2 | 100% | 0% | 100% |  | C2 | 55902.9929 | 0 | 55902.9929
|  | m3/hr | C6 | 161.4949 | 161.4949 | 161.4949 | 161.4949 |  | C3 | 4167 | 4089 | 8256 |  | C3 | 50.47% | 49.53% | 100% |  | C3 | 520875 | 0 | 520875 |  | C3 | 100% | 0% | 100% |  | C3 | 47327.8691 | 0 | 47327.8691
|  | m3/hr | Total | 3166.0872 | 3166.0872 | 3166.0872 | 3166.0872 |  | C4 | 4953 | 3303 | 8256 |  | C4 | 59.99% | 40.01% | 100% |  | C4 | 876681 | 0 | 876681 |  | C4 | 100% | 0% | 100% |  | C4 | 79657.1991 | 0 | 79657.1991
| Average Air Output | % | C1 | 18.55% | 18.55% | 18.55% | 18.55% |  | C5 | 8256 | 0 | 8256 |  | C5 | 100% | 0% | 100% |  | C5 | 2430780.5641 | 0 | 2430780.5641 |  | C5 | 100% | 0% | 100% |  | C5 | 220866.1661 | 0 | 220866.1661
|  | % | C2 | 17.83% | 17.83% | 17.83% | 17.83% |  | C6 | 701 | 7555 | 8256 |  | C6 | 8.491% | 91.51% | 100% |  | C6 | 192074 | 0 | 192074 |  | C6 | 100% | 0% | 100% |  | C6 | 17452.2738 | 0 | 17452.2738
|  | % | C3 | 15.1% | 15.1% | 15.1% | 15.1%
|  | % | C4 | 25.13% | 25.13% | 25.13% | 25.13% | op4 |  |  |  |  | op4 |  |  |  |  | op4 |  |  |  |  | op4 |  |  |  |  | op4
|  | % | C5 | 18.3% | 18.3% | 18.3% | 18.3% |  | C1 | 5120 | 3136 | 8256 |  | C1 | 62.02% | 37.98% | 100% |  | C1 | 836000 | 0 | 836000 |  | C1 | 100% | 0% | 100% |  | C1 | 75960.8323 | 0 | 75960.8323
|  | % | C6 | 5.101% | 5.101% | 5.101% | 5.101% |  | C2 | 4922 | 3334 | 8256 |  | C2 | 59.62% | 40.38% | 100% |  | C2 | 823625 | 0 | 823625 |  | C2 | 100% | 0% | 100% |  | C2 | 74836.4121 | 0 | 74836.4121
|  | % | Total | 100% | 100% | 100% | 100% |  | C3 | 4167 | 4089 | 8256 |  | C3 | 50.47% | 49.53% | 100% |  | C3 | 776437.5 | 0 | 776437.5 |  | C3 | 100% | 0% | 100% |  | C3 | 70548.8502 | 0 | 70548.8502
| Total Energy | kWh | C1 | 836000 | 640000 | 640000 | 836000 |  | C4 | 4953 | 3303 | 8256 |  | C4 | 59.99% | 40.01% | 100% |  | C4 | 1168996.5 | 0 | 1168996.5 |  | C4 | 100% | 0% | 100% |  | C4 | 106217.6401 | 0 | 106217.6401
|  | kWh | C2 | 823625 | 615250 | 615250 | 823625 |  | C5 | 8256 | 0 | 8256 |  | C5 | 100% | 0% | 100% |  | C5 | 2430780.5641 | 0 | 2430780.5641 |  | C5 | 100% | 0% | 100% |  | C5 | 220866.1661 | 0 | 220866.1661
|  | kWh | C3 | 776437.5 | 520875 | 520875 | 776437.5 |  | C6 | 701 | 7555 | 8256 |  | C6 | 8.491% | 91.51% | 100% |  | C6 | 192074 | 1035035 | 1227109 |  | C6 | 15.65% | 84.35% | 100% |  | C6 | 17452.2738 | 94045.5982 | 111497.872
|  | kWh | C4 | 1168996.5 | 876681 | 876681 | 1168996.5
|  | kWh | C5 | 705225.8802 | 705225.8802 | 2430780.5641 | 2430780.5641
|  | kWh | C6 | 1227109 | 192074 | 192074 | 1227109
|  | kWh | Total | 5537393.8802 | 3550105.8802 | 5275660.5641 | 7262948.5641
| Total Energy | % | C1 | 15.1% | 18.03% | 12.13% | 11.51%
|  | % | C2 | 14.87% | 17.33% | 11.66% | 11.34%
|  | % | C3 | 14.02% | 14.67% | 9.873% | 10.69%
|  | % | C4 | 21.11% | 24.69% | 16.62% | 16.1%
|  | % | C5 | 12.74% | 19.86% | 46.08% | 33.47%
|  | % | C6 | 22.16% | 5.41% | 3.641% | 16.9%
|  | % | Total | 100% | 100% | 100% | 100%
| Total Air Output | m3/hr | C1 | 4848640 | 4848640 | 4848640 | 4848640
|  | m3/hr | C2 | 4661134 | 4661134 | 4661134 | 4661134
|  | m3/hr | C3 | 3946149 | 3946149 | 3946149 | 3946149
|  | m3/hr | C4 | 6567678 | 6567678 | 6567678 | 6567678
|  | m3/hr | C5 | 4782313 | 4782313 | 4782313 | 4782313
|  | m3/hr | C6 | 1333302 | 1333302 | 1333302 | 1333302
|  | m3/hr | Total | 26139216 | 26139216 | 26139216 | 26139216
| Total Air Output | % | C1 | 18.55% | 18.55% | 18.55% | 18.55%
|  | % | C2 | 17.83% | 17.83% | 17.83% | 17.83%
|  | % | C3 | 15.1% | 15.1% | 15.1% | 15.1%
|  | % | C4 | 25.13% | 25.13% | 25.13% | 25.13%
|  | % | C5 | 18.3% | 18.3% | 18.3% | 18.3%
|  | % | C6 | 5.101% | 5.101% | 5.101% | 5.101%
|  | % | Total | 100% | 100% | 100% | 100%
| Average Efficiency | kW/m3/hr | C1 | 0.17242 | 0.132 | 0.132 | 0.17242
|  | kW/m3/hr | C2 | 0.1767 | 0.132 | 0.132 | 0.1767
|  | kW/m3/hr | C3 | 0.19676 | 0.132 | 0.132 | 0.19676
|  | kW/m3/hr | C4 | 0.17799 | 0.13348 | 0.13348 | 0.17799
|  | kW/m3/hr | C5 | 0.14747 | 0.14747 | 0.50829 | 0.50829
|  | kW/m3/hr | C6 | 0.92035 | 0.14406 | 0.14406 | 0.92035
|  | kW/m3/hr | Total | 0.21184 | 0.13582 | 0.20183 | 0.27786
| Time Loaded | hrs | C1 | 5120 | 5120 | 5120 | 5120
|  | hrs | C2 | 4922 | 4922 | 4922 | 4922
|  | hrs | C3 | 4167 | 4167 | 4167 | 4167
|  | hrs | C4 | 4953 | 4953 | 4953 | 4953
|  | hrs | C5 | 6816 | 6816 | 8256 | 8256
|  | hrs | C6 | 701 | 701 | 701 | 701
|  | hrs | Total | 26679 | 26679 | 28119 | 28119
| Time Loaded | % | C1 | 62.02% | 62.02% | 62.02% | 62.02%
|  | % | C2 | 59.62% | 59.62% | 59.62% | 59.62%
|  | % | C3 | 50.47% | 50.47% | 50.47% | 50.47%
|  | % | C4 | 59.99% | 59.99% | 59.99% | 59.99%
|  | % | C5 | 82.56% | 82.56% | 100% | 100%
|  | % | C6 | 8.491% | 8.491% | 8.491% | 8.491%
|  | % | Total | 53.86% | 53.86% | 56.76% | 56.76%
| Time Unloaded | hrs | C1 | 3136 | 3136 | 3136 | 3136
|  | hrs | C2 | 3334 | 3334 | 3334 | 3334
|  | hrs | C3 | 4089 | 4089 | 4089 | 4089
|  | hrs | C4 | 3303 | 3303 | 3303 | 3303
|  | hrs | C5 | 1440 | 1440 | 0 | 0
|  | hrs | C6 | 7555 | 7555 | 7555 | 7555
|  | hrs | Total | 22857 | 22857 | 21417 | 21417
| Time Unloaded | % | C1 | 37.98% | 37.98% | 37.98% | 37.98%
|  | % | C2 | 40.38% | 40.38% | 40.38% | 40.38%
|  | % | C3 | 49.53% | 49.53% | 49.53% | 49.53%
|  | % | C4 | 40.01% | 40.01% | 40.01% | 40.01%
|  | % | C5 | 17.44% | 17.44% | 0% | 0%
|  | % | C6 | 91.51% | 91.51% | 91.51% | 91.51%
|  | % | Total | 46.14% | 46.14% | 43.24% | 43.24%
| Total Time | hrs | C1 | 8256 | 8256 | 8256 | 8256
|  | hrs | C2 | 8256 | 8256 | 8256 | 8256
|  | hrs | C3 | 8256 | 8256 | 8256 | 8256
|  | hrs | C4 | 8256 | 8256 | 8256 | 8256
|  | hrs | C5 | 8256 | 8256 | 8256 | 8256
|  | hrs | C6 | 8256 | 8256 | 8256 | 8256
|  | hrs | Total | 49536 | 49536 | 49536 | 49536
| Loaded Energy | kWh | C1 | 836000 | 640000 | 640000 | 836000
|  | kWh | C2 | 823625 | 615250 | 615250 | 823625
|  | kWh | C3 | 776437.5 | 520875 | 520875 | 776437.5
|  | kWh | C4 | 1168996.5 | 876681 | 876681 | 1168996.5
|  | kWh | C5 | 705225.8802 | 705225.8802 | 2430780.5641 | 2430780.5641
|  | kWh | C6 | 192074 | 192074 | 192074 | 192074
|  | kWh | Total | 4502358.8802 | 3550105.8802 | 5275660.5641 | 6227913.5641
| Loaded Energy | % | C1 | 100% | 100% | 100% | 100%
|  | % | C2 | 100% | 100% | 100% | 100%
|  | % | C3 | 100% | 100% | 100% | 100%
|  | % | C4 | 100% | 100% | 100% | 100%
|  | % | C5 | 100% | 100% | 100% | 100%
|  | % | C6 | 15.65% | 100% | 100% | 15.65%
|  | % | Total | 81.31% | 100% | 100% | 85.75%
| Unloaded Energy | kWh | C1 | 0 | 0 | 0 | 0
|  | kWh | C2 | 0 | 0 | 0 | 0
|  | kWh | C3 | 0 | 0 | 0 | 0
|  | kWh | C4 | 0 | 0 | 0 | 0
|  | kWh | C5 | 0 | 0 | 0 | 0
|  | kWh | C6 | 1035035 | 0 | 0 | 1035035
|  | kWh | Total | 1035035 | 0 | 0 | 1035035
| Unloaded Energy | % | C1 | 0% | 0% | 0% | 0%
|  | % | C2 | 0% | 0% | 0% | 0%
|  | % | C3 | 0% | 0% | 0% | 0%
|  | % | C4 | 0% | 0% | 0% | 0%
|  | % | C5 | 0% | 0% | 0% | 0%
|  | % | C6 | 84.35% | 0% | 0% | 84.35%
|  | % | Total | 18.69% | 0% | 0% | 14.25%
| Total Energy | kWh | C1 | 836000 | 640000 | 640000 | 836000
|  | kWh | C2 | 823625 | 615250 | 615250 | 823625
|  | kWh | C3 | 776437.5 | 520875 | 520875 | 776437.5
|  | kWh | C4 | 1168996.5 | 876681 | 876681 | 1168996.5
|  | kWh | C5 | 705225.8802 | 705225.8802 | 2430780.5641 | 2430780.5641
|  | kWh | C6 | 1227109 | 192074 | 192074 | 1227109
|  | kWh | Total | 5537393.8802 | 3550105.8802 | 5275660.5641 | 7262948.5641
| Loaded Cost | £ | C1 | 75960.8323 | 58151.8334 | 58151.8334 | 75960.8323
|  | £ | C2 | 74836.4121 | 55902.9929 | 55902.9929 | 74836.4121
|  | £ | C3 | 70548.8502 | 47327.8691 | 47327.8691 | 70548.8502
|  | £ | C4 | 106217.6401 | 79657.1991 | 79657.1991 | 106217.6401
|  | £ | C5 | 64078.4029 | 64078.4029 | 220866.1661 | 220866.1661
|  | £ | C6 | 17452.2738 | 17452.2738 | 17452.2738 | 17452.2738
|  | £ | Total | 409094.4116 | 322570.5713 | 479358.3345 | 565882.1748
| Unloaded Cost | £ | C1 | 0 | 0 | 0 | 0
|  | £ | C2 | 0 | 0 | 0 | 0
|  | £ | C3 | 0 | 0 | 0 | 0
|  | £ | C4 | 0 | 0 | 0 | 0
|  | £ | C5 | 0 | 0 | 0 | 0
|  | £ | C6 | 94045.5982 | 0 | 0 | 94045.5982
|  | £ | Total | 94045.5982 | 0 | 0 | 94045.5982
| Total Cost | £ | C1 | 75960.8323 | 58151.8334 | 58151.8334 | 75960.8323
|  | £ | C2 | 74836.4121 | 55902.9929 | 55902.9929 | 74836.4121
|  | £ | C3 | 70548.8502 | 47327.8691 | 47327.8691 | 70548.8502
|  | £ | C4 | 106217.6401 | 79657.1991 | 79657.1991 | 106217.6401
|  | £ | C5 | 64078.4029 | 64078.4029 | 220866.1661 | 220866.1661
|  | £ | C6 | 111497.872 | 17452.2738 | 17452.2738 | 111497.872
|  | £ | Total | 503140.0098 | 322570.5713 | 479358.3345 | 659927.773

## Control Scheme 3 Data
Analysis
| 2018 Actual Power Usage: |  | 3633181.008 | kWh
CS3
op1
| Compressor | Control Strategy | Maximum Power | Minimum Power | Maximum Air Output | Minimum Air Output | Average Power | Average Air Output | Total Energy | Total Air Output | Average Efficiency | Time Loaded | Time Loaded | Time Unloaded | Time Unloaded | Loaded Average Power | Loaded Energy | Loaded Energy | Unloaded Energy | Unloaded Energy | Cost of Energy | Loaded Cost | Unloaded Cost | Total Cost | Carbon Used
|  |  | kW | kW | m3/hr | m3/hr | kW | m3/hr | kWh | m3 | kW/m3/hr | hrs | % | hrs | % | kW | kWh | % | kWh | % | £/kWh | £ | £ | £ | Tonnes
| C1 | LoadUnload | 125 | 62 | 947 | 0 | 100.7676 | 579.831 | 831937.5 | 4787085 | 0.17379 | 5055 | 61.23% | 3201 | 38.77% | 100.7676 | 831937.5 | 100% | 0 | 0% | 0.090862 | 75591.7045 | 0 | 75591.7045
| C2 | LoadUnload | 125 | 62 | 947 | 0 | 96.3769 | 513.3024 | 795687.5 | 4237825 | 0.18776 | 4475 | 54.2% | 3781 | 45.8% | 96.3769 | 795687.5 | 100% | 0 | 0% | 0.090862 | 72297.9483 | 0 | 72297.9483
| C3 | LoadUnload | 125 | 62 | 947 | 0 | 87.4213 | 377.6071 | 721750 | 3117524 | 0.23151 | 3292 | 39.87% | 4964 | 60.13% | 87.4213 | 721750 | 100% | 0 | 0% | 0.090862 | 65579.8215 | 0 | 65579.8215
| C4 | LoadUnload | 177 | 88 | 1326 | 0 | 96.0144 | 112.5879 | 792694.5 | 929526 | 0.85279 | 701 | 8.491% | 7555 | 91.51% | 96.0144 | 792694.5 | 100% | 0 | 0% | 0.090862 | 72025.9976 | 0 | 72025.9976
| C5 | VariableSpeed | 384 | 0 | 2604 | 0 | 62.9947 | 427.1831 | 520084.6452 | 3526824 | 0.14747 | 6816 | 82.56% | 1440 | 17.44% | 76.3035 | 520084.6452 | 100% | 0 | 0% | 0.090862 | 47256.0557 | 0 | 47256.0557
| C6 | LoadUnload | 274 | 137 | 1902 | 0 | 220.2355 | 1155.5756 | 1818264 | 9540432 | 0.19059 | 5016 | 60.76% | 3240 | 39.24% | 274 | 1374384 | 75.59% | 443880 | 24.41% | 0.090862 | 124879.6084 | 40331.9309 | 165211.5393
| Total |  | 1210 | 411 | 8673 | 0 | 663.8103 | 3166.0872 | 5480418.1452 | 26139216 | 0.20966 | 25355 | 51.18% | 24181 | 48.82% | 663.8103 | 5036538.1452 | 91.9% | 443880 | 8.099% | 0.090862 | 457631.1359 | 40331.9309 | 497963.0669
op2
| Compressor | Control Strategy | Maximum Power | Minimum Power | Maximum Air Output | Minimum Air Output | Average Power | Average Air Output | Total Energy | Total Air Output | Average Efficiency | Time Loaded | Time Loaded | Time Unloaded | Time Unloaded | Loaded Average Power | Loaded Energy | Loaded Energy | Unloaded Energy | Unloaded Energy | Cost of Energy | Loaded Cost | Unloaded Cost | Total Cost | Carbon Used
|  |  | kW | kW | m3/hr | m3/hr | kW | m3/hr | kWh | m3 | kW/m3/hr | hrs | % | hrs | % | kW | kWh | % | kWh | % | £/kWh | £ | £ | £ | Tonnes
| C1 | OnOff | 125 | 62 | 947 | 0 | 76.5352 | 579.831 | 631875 | 4787085 | 0.132 | 5055 | 61.23% | 3201 | 38.77% | 125 | 631875 | 100% | 0 | 0% | 0.090862 | 57413.5777 | 0 | 58151.8334
| C2 | OnOff | 125 | 62 | 947 | 0 | 67.7538 | 513.3024 | 559375 | 4237825 | 0.132 | 4475 | 54.2% | 3781 | 45.8% | 125 | 559375 | 100% | 0 | 0% | 0.090862 | 50826.0653 | 0 | 55902.9929
| C3 | OnOff | 125 | 62 | 947 | 0 | 49.8425 | 377.6071 | 411500 | 3117524 | 0.132 | 3292 | 39.87% | 4964 | 60.13% | 125 | 411500 | 100% | 0 | 0% | 0.090862 | 37389.8116 | 0 | 47327.8691
| C4 | OnOff | 177 | 88 | 1326 | 0 | 15.0287 | 112.5879 | 124077 | 929526 | 0.13348 | 701 | 8.491% | 7555 | 91.51% | 177 | 124077 | 100% | 0 | 0% | 0.090862 | 11273.9141 | 0 | 79657.1991
| C5 | VariableSpeed | 384 | 0 | 2604 | 0 | 62.9947 | 427.1831 | 520084.6452 | 3526824 | 0.14747 | 6816 | 82.56% | 1440 | 17.44% | 76.3035 | 520084.6452 | 100% | 0 | 0% | 0.090862 | 47256.0557 | 0 | 64078.4029
| C6 | OnOff | 274 | 137 | 1902 | 0 | 166.4709 | 1155.5756 | 1374384 | 9540432 | 0.14406 | 5016 | 60.76% | 3240 | 39.24% | 274 | 1374384 | 100% | 0 | 0% | 0.090862 | 124879.6084 | 0 | 17452.2738
| Total |  | 1210 | 411 | 8673 | 0 | 438.6259 | 3166.0872 | 3621295.6452 | 26139216 | 0.13854 | 25355 | 51.18% | 24181 | 48.82% | 712.5674 | 3621295.6452 | 100% | 0 | 0% | 0.090862 | 329039.0327 | 0 | 322570.5713
op3
| Compressor | Control Strategy | Maximum Power | Minimum Power | Maximum Air Output | Minimum Air Output | Average Power | Average Air Output | Total Energy | Total Air Output | Average Efficiency | Time Loaded | Time Loaded | Time Unloaded | Time Unloaded | Loaded Average Power | Loaded Energy | Loaded Energy | Unloaded Energy | Unloaded Energy | Cost of Energy | Loaded Cost | Unloaded Cost | Total Cost | Carbon Used
|  |  | kW | kW | m3/hr | m3/hr | kW | m3/hr | kWh | m3 | kW/m3/hr | hrs | % | hrs | % | kW | kWh | % | kWh | % | £/kWh | £ | £ | £ | Tonnes
| C1 | OnOff | 125 | 62 | 947 | 0 | 76.5352 | 579.831 | 631875 | 4787085 | 0.132 | 5055 | 61.23% | 3201 | 38.77% | 125 | 631875 | 100% | 0 | 0% | 0.090862 | 57413.5777 | 0 | 57413.5777
| C2 | OnOff | 125 | 62 | 947 | 0 | 67.7538 | 513.3024 | 559375 | 4237825 | 0.132 | 4475 | 54.2% | 3781 | 45.8% | 125 | 559375 | 100% | 0 | 0% | 0.090862 | 50826.0653 | 0 | 50826.0653
| C3 | OnOff | 125 | 62 | 947 | 0 | 49.8425 | 377.6071 | 411500 | 3117524 | 0.132 | 3292 | 39.87% | 4964 | 60.13% | 125 | 411500 | 100% | 0 | 0% | 0.090862 | 37389.8116 | 0 | 37389.8116
| C4 | OnOff | 177 | 88 | 1326 | 0 | 15.0287 | 112.5879 | 124077 | 929526 | 0.13348 | 701 | 8.491% | 7555 | 91.51% | 177 | 124077 | 100% | 0 | 0% | 0.090862 | 11273.9141 | 0 | 11273.9141
| C5 | InletModulation | 384 | 0 | 2604 | 0 | 287.6984 | 427.1831 | 2375238.1935 | 3526824 | 0.67348 | 8256 | 100% | 0 | 0% | 287.6984 | 2375238.1935 | 100% | 0 | 0% | 0.090862 | 215819.462 | 0 | 215819.462
| C6 | OnOff | 274 | 137 | 1902 | 0 | 166.4709 | 1155.5756 | 1374384 | 9540432 | 0.14406 | 5016 | 60.76% | 3240 | 39.24% | 274 | 1374384 | 100% | 0 | 0% | 0.090862 | 124879.6084 | 0 | 124879.6084
| Total |  | 1210 | 411 | 8673 | 0 | 663.3296 | 3166.0872 | 5476449.1935 | 26139216 | 0.20951 | 26795 | 54.09% | 22741 | 45.91% | 900.475 | 5476449.1935 | 100% | 0 | 0% | 0.090862 | 497602.439 | 0 | 497602.439
op4
| Compressor | Control Strategy | Maximum Power | Minimum Power | Maximum Air Output | Minimum Air Output | Average Power | Average Air Output | Total Energy | Total Air Output | Average Efficiency | Time Loaded | Time Loaded | Time Unloaded | Time Unloaded | Loaded Average Power | Loaded Energy | Loaded Energy | Unloaded Energy | Unloaded Energy | Cost of Energy | Loaded Cost | Unloaded Cost | Total Cost | Carbon Used
|  |  | kW | kW | m3/hr | m3/hr | kW | m3/hr | kWh | m3 | kW/m3/hr | hrs | % | hrs | % | kW | kWh | % | kWh | % | £/kWh | £ | £ | £ | Tonnes
| C1 | LoadUnload | 125 | 62 | 947 | 0 | 100.7676 | 579.831 | 831937.5 | 4787085 | 0.17379 | 5055 | 61.23% | 3201 | 38.77% | 100.7676 | 831937.5 | 100% | 0 | 0% | 0.090862 | 75591.7045 | 0 | 75591.7045
| C2 | LoadUnload | 125 | 62 | 947 | 0 | 96.3769 | 513.3024 | 795687.5 | 4237825 | 0.18776 | 4475 | 54.2% | 3781 | 45.8% | 96.3769 | 795687.5 | 100% | 0 | 0% | 0.090862 | 72297.9483 | 0 | 72297.9483
| C3 | LoadUnload | 125 | 62 | 947 | 0 | 87.4213 | 377.6071 | 721750 | 3117524 | 0.23151 | 3292 | 39.87% | 4964 | 60.13% | 87.4213 | 721750 | 100% | 0 | 0% | 0.090862 | 65579.8215 | 0 | 65579.8215
| C4 | LoadUnload | 177 | 88 | 1326 | 0 | 96.0144 | 112.5879 | 792694.5 | 929526 | 0.85279 | 701 | 8.491% | 7555 | 91.51% | 96.0144 | 792694.5 | 100% | 0 | 0% | 0.090862 | 72025.9976 | 0 | 72025.9976
| C5 | InletModulation | 384 | 0 | 2604 | 0 | 287.6984 | 427.1831 | 2375238.1935 | 3526824 | 0.67348 | 8256 | 100% | 0 | 0% | 287.6984 | 2375238.1935 | 100% | 0 | 0% | 0.090862 | 215819.462 | 0 | 215819.462
| C6 | LoadUnload | 274 | 137 | 1902 | 0 | 220.2355 | 1155.5756 | 1818264 | 9540432 | 0.19059 | 5016 | 60.76% | 3240 | 39.24% | 274 | 1374384 | 75.59% | 443880 | 24.41% | 0.090862 | 124879.6084 | 40331.9309 | 165211.5393
| Total |  | 1210 | 411 | 8673 | 0 | 888.514 | 3166.0872 | 7335571.6935 | 26139216 | 0.28063 | 26795 | 54.09% | 22741 | 45.91% | 888.514 | 6891691.6935 | 93.95% | 443880 | 6.051% | 0.090862 | 626194.5422 | 40331.9309 | 666526.4732

## Control Scheme 3 Graphs
Analysis
| 2018 Actual Power Usage: |  | 3633181.008 | kWh
CS3
| LU+VS Data | Units | Compressors | op1 | op2 | op3 | op4 |  |  | Time Loaded | Time Unloaded | Total |  |  | Time Loaded | Time Unloaded | Total |  |  | Loaded Energy | Unloaded Energy | Total |  |  | Loaded Energy | Unloaded Energy | Total |  |  | Loaded Cost | Unloaded Cost | Total
| Average Power | kW | C1 | 100.7676 | 76.5352 | 76.5352 | 100.7676 | op1 |  |  |  |  | op1 |  |  |  |  | op1 |  |  |  |  | op1 |  |  |  |  | op1
|  | kW | C2 | 96.3769 | 67.7538 | 67.7538 | 96.3769 |  | C1 | 5055 | 3201 | 8256 |  | C1 | 61.23% | 38.77% | 100% |  | C1 | 831937.5 | 0 | 831937.5 |  | C1 | 100% | 0% | 100% |  | C1 | 75591.7045 | 0 | 75591.7045
|  | kW | C3 | 87.4213 | 49.8425 | 49.8425 | 87.4213 |  | C2 | 4475 | 3781 | 8256 |  | C2 | 54.2% | 45.8% | 100% |  | C2 | 795687.5 | 0 | 795687.5 |  | C2 | 100% | 0% | 100% |  | C2 | 72297.9483 | 0 | 72297.9483
|  | kW | C4 | 96.0144 | 15.0287 | 15.0287 | 96.0144 |  | C3 | 3292 | 4964 | 8256 |  | C3 | 39.87% | 60.13% | 100% |  | C3 | 721750 | 0 | 721750 |  | C3 | 100% | 0% | 100% |  | C3 | 65579.8215 | 0 | 65579.8215
|  | kW | C5 | 62.9947 | 62.9947 | 287.6984 | 287.6984 |  | C4 | 701 | 7555 | 8256 |  | C4 | 8.491% | 91.51% | 100% |  | C4 | 792694.5 | 0 | 792694.5 |  | C4 | 100% | 0% | 100% |  | C4 | 72025.9976 | 0 | 72025.9976
|  | kW | C6 | 220.2355 | 166.4709 | 166.4709 | 220.2355 |  | C5 | 6816 | 1440 | 8256 |  | C5 | 82.56% | 17.44% | 100% |  | C5 | 520084.6452 | 0 | 520084.6452 |  | C5 | 100% | 0% | 100% |  | C5 | 47256.0557 | 0 | 47256.0557
|  | kW | Total | 663.8103 | 438.6259 | 663.3296 | 888.514 |  | C6 | 5016 | 3240 | 8256 |  | C6 | 60.76% | 39.24% | 100% |  | C6 | 1374384 | 443880 | 1818264 |  | C6 | 75.59% | 24.41% | 100% |  | C6 | 124879.6084 | 40331.9309 | 165211.5393
| Average Power | % | C1 | 15.18% | 17.45% | 11.54% | 11.34%
|  | % | C2 | 14.52% | 15.45% | 10.21% | 10.85% | op2 |  |  |  |  | op2 |  |  |  |  | op2 |  |  |  |  | op2 |  |  |  |  | op2
|  | % | C3 | 13.17% | 11.36% | 7.514% | 9.839% |  | C1 | 5055 | 3201 | 8256 |  | C1 | 61.23% | 38.77% | 100% |  | C1 | 631875 | 0 | 631875 |  | C1 | 100% | 0% | 100% |  | C1 | 57413.5777 | 0 | 57413.5777
|  | % | C4 | 14.46% | 3.426% | 2.266% | 10.81% |  | C2 | 4475 | 3781 | 8256 |  | C2 | 54.2% | 45.8% | 100% |  | C2 | 559375 | 0 | 559375 |  | C2 | 100% | 0% | 100% |  | C2 | 50826.0653 | 0 | 50826.0653
|  | % | C5 | 9.49% | 14.36% | 43.37% | 32.38% |  | C3 | 3292 | 4964 | 8256 |  | C3 | 39.87% | 60.13% | 100% |  | C3 | 411500 | 0 | 411500 |  | C3 | 100% | 0% | 100% |  | C3 | 37389.8116 | 0 | 37389.8116
|  | % | C6 | 33.18% | 37.95% | 25.1% | 24.79% |  | C4 | 701 | 7555 | 8256 |  | C4 | 8.491% | 91.51% | 100% |  | C4 | 124077 | 0 | 124077 |  | C4 | 100% | 0% | 100% |  | C4 | 11273.9141 | 0 | 11273.9141
|  | % | Total | 100% | 100% | 100% | 100% |  | C5 | 6816 | 1440 | 8256 |  | C5 | 82.56% | 17.44% | 100% |  | C5 | 520084.6452 | 0 | 520084.6452 |  | C5 | 100% | 0% | 100% |  | C5 | 47256.0557 | 0 | 47256.0557
| Average Air Output | m3/hr | C1 | 579.831 | 579.831 | 579.831 | 579.831 |  | C6 | 5016 | 3240 | 8256 |  | C6 | 60.76% | 39.24% | 100% |  | C6 | 1374384 | 0 | 1374384 |  | C6 | 100% | 0% | 100% |  | C6 | 124879.6084 | 0 | 124879.6084
|  | m3/hr | C2 | 513.3024 | 513.3024 | 513.3024 | 513.3024
|  | m3/hr | C3 | 377.6071 | 377.6071 | 377.6071 | 377.6071 | op3 |  |  |  |  | op3 |  |  |  |  | op3 |  |  |  |  | op3 |  |  |  |  | op3
|  | m3/hr | C4 | 112.5879 | 112.5879 | 112.5879 | 112.5879 |  | C1 | 5055 | 3201 | 8256 |  | C1 | 61.23% | 38.77% | 100% |  | C1 | 631875 | 0 | 631875 |  | C1 | 100% | 0% | 100% |  | C1 | 57413.5777 | 0 | 57413.5777
|  | m3/hr | C5 | 427.1831 | 427.1831 | 427.1831 | 427.1831 |  | C2 | 4475 | 3781 | 8256 |  | C2 | 54.2% | 45.8% | 100% |  | C2 | 559375 | 0 | 559375 |  | C2 | 100% | 0% | 100% |  | C2 | 50826.0653 | 0 | 50826.0653
|  | m3/hr | C6 | 1155.5756 | 1155.5756 | 1155.5756 | 1155.5756 |  | C3 | 3292 | 4964 | 8256 |  | C3 | 39.87% | 60.13% | 100% |  | C3 | 411500 | 0 | 411500 |  | C3 | 100% | 0% | 100% |  | C3 | 37389.8116 | 0 | 37389.8116
|  | m3/hr | Total | 3166.0872 | 3166.0872 | 3166.0872 | 3166.0872 |  | C4 | 701 | 7555 | 8256 |  | C4 | 8.491% | 91.51% | 100% |  | C4 | 124077 | 0 | 124077 |  | C4 | 100% | 0% | 100% |  | C4 | 11273.9141 | 0 | 11273.9141
| Average Air Output | % | C1 | 18.31% | 18.31% | 18.31% | 18.31% |  | C5 | 8256 | 0 | 8256 |  | C5 | 100% | 0% | 100% |  | C5 | 2375238.1935 | 0 | 2375238.1935 |  | C5 | 100% | 0% | 100% |  | C5 | 215819.462 | 0 | 215819.462
|  | % | C2 | 16.21% | 16.21% | 16.21% | 16.21% |  | C6 | 5016 | 3240 | 8256 |  | C6 | 60.76% | 39.24% | 100% |  | C6 | 1374384 | 0 | 1374384 |  | C6 | 100% | 0% | 100% |  | C6 | 124879.6084 | 0 | 124879.6084
|  | % | C3 | 11.93% | 11.93% | 11.93% | 11.93%
|  | % | C4 | 3.556% | 3.556% | 3.556% | 3.556% | op4 |  |  |  |  | op4 |  |  |  |  | op4 |  |  |  |  | op4 |  |  |  |  | op4
|  | % | C5 | 13.49% | 13.49% | 13.49% | 13.49% |  | C1 | 5055 | 3201 | 8256 |  | C1 | 61.23% | 38.77% | 100% |  | C1 | 831937.5 | 0 | 831937.5 |  | C1 | 100% | 0% | 100% |  | C1 | 75591.7045 | 0 | 75591.7045
|  | % | C6 | 36.5% | 36.5% | 36.5% | 36.5% |  | C2 | 4475 | 3781 | 8256 |  | C2 | 54.2% | 45.8% | 100% |  | C2 | 795687.5 | 0 | 795687.5 |  | C2 | 100% | 0% | 100% |  | C2 | 72297.9483 | 0 | 72297.9483
|  | % | Total | 100% | 100% | 100% | 100% |  | C3 | 3292 | 4964 | 8256 |  | C3 | 39.87% | 60.13% | 100% |  | C3 | 721750 | 0 | 721750 |  | C3 | 100% | 0% | 100% |  | C3 | 65579.8215 | 0 | 65579.8215
| Total Energy | kWh | C1 | 831937.5 | 631875 | 631875 | 831937.5 |  | C4 | 701 | 7555 | 8256 |  | C4 | 8.491% | 91.51% | 100% |  | C4 | 792694.5 | 0 | 792694.5 |  | C4 | 100% | 0% | 100% |  | C4 | 72025.9976 | 0 | 72025.9976
|  | kWh | C2 | 795687.5 | 559375 | 559375 | 795687.5 |  | C5 | 8256 | 0 | 8256 |  | C5 | 100% | 0% | 100% |  | C5 | 2375238.1935 | 0 | 2375238.1935 |  | C5 | 100% | 0% | 100% |  | C5 | 215819.462 | 0 | 215819.462
|  | kWh | C3 | 721750 | 411500 | 411500 | 721750 |  | C6 | 5016 | 3240 | 8256 |  | C6 | 60.76% | 39.24% | 100% |  | C6 | 1374384 | 443880 | 1818264 |  | C6 | 75.59% | 24.41% | 100% |  | C6 | 124879.6084 | 40331.9309 | 165211.5393
|  | kWh | C4 | 792694.5 | 124077 | 124077 | 792694.5
|  | kWh | C5 | 520084.6452 | 520084.6452 | 2375238.1935 | 2375238.1935
|  | kWh | C6 | 1818264 | 1374384 | 1374384 | 1818264
|  | kWh | Total | 5480418.1452 | 3621295.6452 | 5476449.1935 | 7335571.6935
| Total Energy | % | C1 | 15.18% | 17.45% | 11.54% | 11.34%
|  | % | C2 | 14.52% | 15.45% | 10.21% | 10.85%
|  | % | C3 | 13.17% | 11.36% | 7.514% | 9.839%
|  | % | C4 | 14.46% | 3.426% | 2.266% | 10.81%
|  | % | C5 | 9.49% | 14.36% | 43.37% | 32.38%
|  | % | C6 | 33.18% | 37.95% | 25.1% | 24.79%
|  | % | Total | 100% | 100% | 100% | 100%
| Total Air Output | m3/hr | C1 | 4787085 | 4787085 | 4787085 | 4787085
|  | m3/hr | C2 | 4237825 | 4237825 | 4237825 | 4237825
|  | m3/hr | C3 | 3117524 | 3117524 | 3117524 | 3117524
|  | m3/hr | C4 | 929526 | 929526 | 929526 | 929526
|  | m3/hr | C5 | 3526824 | 3526824 | 3526824 | 3526824
|  | m3/hr | C6 | 9540432 | 9540432 | 9540432 | 9540432
|  | m3/hr | Total | 26139216 | 26139216 | 26139216 | 26139216
| Total Air Output | % | C1 | 18.31% | 18.31% | 18.31% | 18.31%
|  | % | C2 | 16.21% | 16.21% | 16.21% | 16.21%
|  | % | C3 | 11.93% | 11.93% | 11.93% | 11.93%
|  | % | C4 | 3.556% | 3.556% | 3.556% | 3.556%
|  | % | C5 | 13.49% | 13.49% | 13.49% | 13.49%
|  | % | C6 | 36.5% | 36.5% | 36.5% | 36.5%
|  | % | Total | 100% | 100% | 100% | 100%
| Average Efficiency | kW/m3/hr | C1 | 0.17379 | 0.132 | 0.132 | 0.17379
|  | kW/m3/hr | C2 | 0.18776 | 0.132 | 0.132 | 0.18776
|  | kW/m3/hr | C3 | 0.23151 | 0.132 | 0.132 | 0.23151
|  | kW/m3/hr | C4 | 0.85279 | 0.13348 | 0.13348 | 0.85279
|  | kW/m3/hr | C5 | 0.14747 | 0.14747 | 0.67348 | 0.67348
|  | kW/m3/hr | C6 | 0.19059 | 0.14406 | 0.14406 | 0.19059
|  | kW/m3/hr | Total | 0.20966 | 0.13854 | 0.20951 | 0.28063
| Time Loaded | hrs | C1 | 5055 | 5055 | 5055 | 5055
|  | hrs | C2 | 4475 | 4475 | 4475 | 4475
|  | hrs | C3 | 3292 | 3292 | 3292 | 3292
|  | hrs | C4 | 701 | 701 | 701 | 701
|  | hrs | C5 | 6816 | 6816 | 8256 | 8256
|  | hrs | C6 | 5016 | 5016 | 5016 | 5016
|  | hrs | Total | 25355 | 25355 | 26795 | 26795
| Time Loaded | % | C1 | 61.23% | 61.23% | 61.23% | 61.23%
|  | % | C2 | 54.2% | 54.2% | 54.2% | 54.2%
|  | % | C3 | 39.87% | 39.87% | 39.87% | 39.87%
|  | % | C4 | 8.491% | 8.491% | 8.491% | 8.491%
|  | % | C5 | 82.56% | 82.56% | 100% | 100%
|  | % | C6 | 60.76% | 60.76% | 60.76% | 60.76%
|  | % | Total | 51.18% | 51.18% | 54.09% | 54.09%
| Time Unloaded | hrs | C1 | 3201 | 3201 | 3201 | 3201
|  | hrs | C2 | 3781 | 3781 | 3781 | 3781
|  | hrs | C3 | 4964 | 4964 | 4964 | 4964
|  | hrs | C4 | 7555 | 7555 | 7555 | 7555
|  | hrs | C5 | 1440 | 1440 | 0 | 0
|  | hrs | C6 | 3240 | 3240 | 3240 | 3240
|  | hrs | Total | 24181 | 24181 | 22741 | 22741
| Time Unloaded | % | C1 | 38.77% | 38.77% | 38.77% | 38.77%
|  | % | C2 | 45.8% | 45.8% | 45.8% | 45.8%
|  | % | C3 | 60.13% | 60.13% | 60.13% | 60.13%
|  | % | C4 | 91.51% | 91.51% | 91.51% | 91.51%
|  | % | C5 | 17.44% | 17.44% | 0% | 0%
|  | % | C6 | 39.24% | 39.24% | 39.24% | 39.24%
|  | % | Total | 48.82% | 48.82% | 45.91% | 45.91%
| Total Time | hrs | C1 | 8256 | 8256 | 8256 | 8256
|  | hrs | C2 | 8256 | 8256 | 8256 | 8256
|  | hrs | C3 | 8256 | 8256 | 8256 | 8256
|  | hrs | C4 | 8256 | 8256 | 8256 | 8256
|  | hrs | C5 | 8256 | 8256 | 8256 | 8256
|  | hrs | C6 | 8256 | 8256 | 8256 | 8256
|  | hrs | Total | 49536 | 49536 | 49536 | 49536
| Loaded Energy | kWh | C1 | 831937.5 | 631875 | 631875 | 831937.5
|  | kWh | C2 | 795687.5 | 559375 | 559375 | 795687.5
|  | kWh | C3 | 721750 | 411500 | 411500 | 721750
|  | kWh | C4 | 792694.5 | 124077 | 124077 | 792694.5
|  | kWh | C5 | 520084.6452 | 520084.6452 | 2375238.1935 | 2375238.1935
|  | kWh | C6 | 1374384 | 1374384 | 1374384 | 1374384
|  | kWh | Total | 5036538.1452 | 3621295.6452 | 5476449.1935 | 6891691.6935
| Loaded Energy | % | C1 | 100% | 100% | 100% | 100%
|  | % | C2 | 100% | 100% | 100% | 100%
|  | % | C3 | 100% | 100% | 100% | 100%
|  | % | C4 | 100% | 100% | 100% | 100%
|  | % | C5 | 100% | 100% | 100% | 100%
|  | % | C6 | 75.59% | 100% | 100% | 75.59%
|  | % | Total | 91.9% | 100% | 100% | 93.95%
| Unloaded Energy | kWh | C1 | 0 | 0 | 0 | 0
|  | kWh | C2 | 0 | 0 | 0 | 0
|  | kWh | C3 | 0 | 0 | 0 | 0
|  | kWh | C4 | 0 | 0 | 0 | 0
|  | kWh | C5 | 0 | 0 | 0 | 0
|  | kWh | C6 | 443880 | 0 | 0 | 443880
|  | kWh | Total | 443880 | 0 | 0 | 443880
| Unloaded Energy | % | C1 | 0% | 0% | 0% | 0%
|  | % | C2 | 0% | 0% | 0% | 0%
|  | % | C3 | 0% | 0% | 0% | 0%
|  | % | C4 | 0% | 0% | 0% | 0%
|  | % | C5 | 0% | 0% | 0% | 0%
|  | % | C6 | 24.41% | 0% | 0% | 24.41%
|  | % | Total | 8.099% | 0% | 0% | 6.051%
| Total Energy | kWh | C1 | 831937.5 | 631875 | 631875 | 831937.5
|  | kWh | C2 | 795687.5 | 559375 | 559375 | 795687.5
|  | kWh | C3 | 721750 | 411500 | 411500 | 721750
|  | kWh | C4 | 792694.5 | 124077 | 124077 | 792694.5
|  | kWh | C5 | 520084.6452 | 520084.6452 | 2375238.1935 | 2375238.1935
|  | kWh | C6 | 1818264 | 1374384 | 1374384 | 1818264
|  | kWh | Total | 5480418.1452 | 3621295.6452 | 5476449.1935 | 7335571.6935
| Loaded Cost | £ | C1 | 75591.7045 | 57413.5777 | 57413.5777 | 75591.7045
|  | £ | C2 | 72297.9483 | 50826.0653 | 50826.0653 | 72297.9483
|  | £ | C3 | 65579.8215 | 37389.8116 | 37389.8116 | 65579.8215
|  | £ | C4 | 72025.9976 | 11273.9141 | 11273.9141 | 72025.9976
|  | £ | C5 | 47256.0557 | 47256.0557 | 215819.462 | 215819.462
|  | £ | C6 | 124879.6084 | 124879.6084 | 124879.6084 | 124879.6084
|  | £ | Total | 457631.1359 | 329039.0327 | 497602.439 | 626194.5422
| Unloaded Cost | £ | C1 | 0 | 0 | 0 | 0
|  | £ | C2 | 0 | 0 | 0 | 0
|  | £ | C3 | 0 | 0 | 0 | 0
|  | £ | C4 | 0 | 0 | 0 | 0
|  | £ | C5 | 0 | 0 | 0 | 0
|  | £ | C6 | 40331.9309 | 0 | 0 | 40331.9309
|  | £ | Total | 40331.9309 | 0 | 0 | 40331.9309
| Total Cost | £ | C1 | 75591.7045 | 58151.8334 | 57413.5777 | 75591.7045
|  | £ | C2 | 72297.9483 | 55902.9929 | 50826.0653 | 72297.9483
|  | £ | C3 | 65579.8215 | 47327.8691 | 37389.8116 | 65579.8215
|  | £ | C4 | 72025.9976 | 79657.1991 | 11273.9141 | 72025.9976
|  | £ | C5 | 47256.0557 | 64078.4029 | 215819.462 | 215819.462
|  | £ | C6 | 165211.5393 | 17452.2738 | 124879.6084 | 165211.5393
|  | £ | Total | 497963.0669 | 322570.5713 | 497602.439 | 666526.4732

## Control Scheme 4 Data
Analysis
| 2018 Actual Power Usage: |  | 3633181.008 | kWh
CS4
op1
| Compressor | Control Strategy | Maximum Power | Minimum Power | Maximum Air Output | Minimum Air Output | Average Power | Average Air Output | Total Energy | Total Air Output | Average Efficiency | Time Loaded | Time Loaded | Time Unloaded | Time Unloaded | Loaded Average Power | Loaded Energy | Loaded Energy | Unloaded Energy | Unloaded Energy | Cost of Energy | Loaded Cost | Unloaded Cost | Total Cost | Carbon Used
|  |  | kW | kW | m3/hr | m3/hr | kW | m3/hr | kWh | m3 | kW/m3/hr | hrs | % | hrs | % | kW | kWh | % | kWh | % | £/kWh | £ | £ | £ | Tonnes
| C1 | LoadUnload | 125 | 62 | 947 | 0 | 100.7676 | 579.831 | 831937.5 | 4787085 | 0.17379 | 5055 | 61.23% | 3201 | 38.77% | 100.7676 | 831937.5 | 100% | 0 | 0% | 0.090862 | 75591.7045 | 0 | 75591.7045
| C2 | LoadUnload | 125 | 62 | 947 | 0 | 96.3769 | 513.3024 | 795687.5 | 4237825 | 0.18776 | 4475 | 54.2% | 3781 | 45.8% | 96.3769 | 795687.5 | 100% | 0 | 0% | 0.090862 | 72297.9483 | 0 | 72297.9483
| C3 | LoadUnload | 125 | 62 | 947 | 0 | 87.4213 | 377.6071 | 721750 | 3117524 | 0.23151 | 3292 | 39.87% | 4964 | 60.13% | 87.4213 | 721750 | 100% | 0 | 0% | 0.090862 | 65579.8215 | 0 | 65579.8215
| C4 | LoadUnload | 177 | 88 | 1326 | 0 | 96.0144 | 112.5879 | 792694.5 | 929526 | 0.85279 | 701 | 8.491% | 7555 | 91.51% | 96.0144 | 792694.5 | 100% | 0 | 0% | 0.090862 | 72025.9976 | 0 | 72025.9976
| C5 | VariableSpeed | 384 | 0 | 2604 | 0 | 62.9947 | 427.1831 | 520084.6452 | 3526824 | 0.14747 | 6816 | 82.56% | 1440 | 17.44% | 76.3035 | 520084.6452 | 100% | 0 | 0% | 0.090862 | 47256.0557 | 0 | 47256.0557
| C6 | LoadUnload | 274 | 137 | 1902 | 0 | 220.2355 | 1155.5756 | 1818264 | 9540432 | 0.19059 | 5016 | 60.76% | 3240 | 39.24% | 274 | 1374384 | 75.59% | 443880 | 24.41% | 0.090862 | 124879.6084 | 40331.9309 | 165211.5393
| Total |  | 1210 | 411 | 8673 | 0 | 663.8103 | 3166.0872 | 5480418.1452 | 26139216 | 0.20966 | 25355 | 51.18% | 24181 | 48.82% | 663.8103 | 5036538.1452 | 91.9% | 443880 | 8.099% | 0.090862 | 457631.1359 | 40331.9309 | 497963.0669
op2
| Compressor | Control Strategy | Maximum Power | Minimum Power | Maximum Air Output | Minimum Air Output | Average Power | Average Air Output | Total Energy | Total Air Output | Average Efficiency | Time Loaded | Time Loaded | Time Unloaded | Time Unloaded | Loaded Average Power | Loaded Energy | Loaded Energy | Unloaded Energy | Unloaded Energy | Cost of Energy | Loaded Cost | Unloaded Cost | Total Cost | Carbon Used
|  |  | kW | kW | m3/hr | m3/hr | kW | m3/hr | kWh | m3 | kW/m3/hr | hrs | % | hrs | % | kW | kWh | % | kWh | % | £/kWh | £ | £ | £ | Tonnes
| C1 | OnOff | 125 | 62 | 947 | 0 | 76.5352 | 579.831 | 631875 | 4787085 | 0.132 | 5055 | 61.23% | 3201 | 38.77% | 125 | 631875 | 100% | 0 | 0% | 0.090862 | 57413.5777 | 0 | 58151.8334
| C2 | OnOff | 125 | 62 | 947 | 0 | 67.7538 | 513.3024 | 559375 | 4237825 | 0.132 | 4475 | 54.2% | 3781 | 45.8% | 125 | 559375 | 100% | 0 | 0% | 0.090862 | 50826.0653 | 0 | 55902.9929
| C3 | OnOff | 125 | 62 | 947 | 0 | 49.8425 | 377.6071 | 411500 | 3117524 | 0.132 | 3292 | 39.87% | 4964 | 60.13% | 125 | 411500 | 100% | 0 | 0% | 0.090862 | 37389.8116 | 0 | 47327.8691
| C4 | OnOff | 177 | 88 | 1326 | 0 | 15.0287 | 112.5879 | 124077 | 929526 | 0.13348 | 701 | 8.491% | 7555 | 91.51% | 177 | 124077 | 100% | 0 | 0% | 0.090862 | 11273.9141 | 0 | 79657.1991
| C5 | VariableSpeed | 384 | 0 | 2604 | 0 | 62.9947 | 427.1831 | 520084.6452 | 3526824 | 0.14747 | 6816 | 82.56% | 1440 | 17.44% | 76.3035 | 520084.6452 | 100% | 0 | 0% | 0.090862 | 47256.0557 | 0 | 64078.4029
| C6 | OnOff | 274 | 137 | 1902 | 0 | 166.4709 | 1155.5756 | 1374384 | 9540432 | 0.14406 | 5016 | 60.76% | 3240 | 39.24% | 274 | 1374384 | 100% | 0 | 0% | 0.090862 | 124879.6084 | 0 | 17452.2738
| Total |  | 1210 | 411 | 8673 | 0 | 438.6259 | 3166.0872 | 3621295.6452 | 26139216 | 0.13854 | 25355 | 51.18% | 24181 | 48.82% | 712.5674 | 3621295.6452 | 100% | 0 | 0% | 0.090862 | 329039.0327 | 0 | 322570.5713
op3
| Compressor | Control Strategy | Maximum Power | Minimum Power | Maximum Air Output | Minimum Air Output | Average Power | Average Air Output | Total Energy | Total Air Output | Average Efficiency | Time Loaded | Time Loaded | Time Unloaded | Time Unloaded | Loaded Average Power | Loaded Energy | Loaded Energy | Unloaded Energy | Unloaded Energy | Cost of Energy | Loaded Cost | Unloaded Cost | Total Cost | Carbon Used
|  |  | kW | kW | m3/hr | m3/hr | kW | m3/hr | kWh | m3 | kW/m3/hr | hrs | % | hrs | % | kW | kWh | % | kWh | % | £/kWh | £ | £ | £ | Tonnes
| C1 | OnOff | 125 | 62 | 947 | 0 | 76.5352 | 579.831 | 631875 | 4787085 | 0.132 | 5055 | 61.23% | 3201 | 38.77% | 125 | 631875 | 100% | 0 | 0% | 0.090862 | 57413.5777 | 0 | 57413.5777
| C2 | OnOff | 125 | 62 | 947 | 0 | 67.7538 | 513.3024 | 559375 | 4237825 | 0.132 | 4475 | 54.2% | 3781 | 45.8% | 125 | 559375 | 100% | 0 | 0% | 0.090862 | 50826.0653 | 0 | 50826.0653
| C3 | OnOff | 125 | 62 | 947 | 0 | 49.8425 | 377.6071 | 411500 | 3117524 | 0.132 | 3292 | 39.87% | 4964 | 60.13% | 125 | 411500 | 100% | 0 | 0% | 0.090862 | 37389.8116 | 0 | 37389.8116
| C4 | OnOff | 177 | 88 | 1326 | 0 | 15.0287 | 112.5879 | 124077 | 929526 | 0.13348 | 701 | 8.491% | 7555 | 91.51% | 177 | 124077 | 100% | 0 | 0% | 0.090862 | 11273.9141 | 0 | 11273.9141
| C5 | InletModulation | 384 | 0 | 2604 | 0 | 287.6984 | 427.1831 | 2375238.1935 | 3526824 | 0.67348 | 8256 | 100% | 0 | 0% | 287.6984 | 2375238.1935 | 100% | 0 | 0% | 0.090862 | 215819.462 | 0 | 215819.462
| C6 | OnOff | 274 | 137 | 1902 | 0 | 166.4709 | 1155.5756 | 1374384 | 9540432 | 0.14406 | 5016 | 60.76% | 3240 | 39.24% | 274 | 1374384 | 100% | 0 | 0% | 0.090862 | 124879.6084 | 0 | 124879.6084
| Total |  | 1210 | 411 | 8673 | 0 | 663.3296 | 3166.0872 | 5476449.1935 | 26139216 | 0.20951 | 26795 | 54.09% | 22741 | 45.91% | 900.475 | 5476449.1935 | 100% | 0 | 0% | 0.090862 | 497602.439 | 0 | 497602.439
op4
| Compressor | Control Strategy | Maximum Power | Minimum Power | Maximum Air Output | Minimum Air Output | Average Power | Average Air Output | Total Energy | Total Air Output | Average Efficiency | Time Loaded | Time Loaded | Time Unloaded | Time Unloaded | Loaded Average Power | Loaded Energy | Loaded Energy | Unloaded Energy | Unloaded Energy | Cost of Energy | Loaded Cost | Unloaded Cost | Total Cost | Carbon Used
|  |  | kW | kW | m3/hr | m3/hr | kW | m3/hr | kWh | m3 | kW/m3/hr | hrs | % | hrs | % | kW | kWh | % | kWh | % | £/kWh | £ | £ | £ | Tonnes
| C1 | LoadUnload | 125 | 62 | 947 | 0 | 100.7676 | 579.831 | 831937.5 | 4787085 | 0.17379 | 5055 | 61.23% | 3201 | 38.77% | 100.7676 | 831937.5 | 100% | 0 | 0% | 0.090862 | 75591.7045 | 0 | 75591.7045
| C2 | LoadUnload | 125 | 62 | 947 | 0 | 96.3769 | 513.3024 | 795687.5 | 4237825 | 0.18776 | 4475 | 54.2% | 3781 | 45.8% | 96.3769 | 795687.5 | 100% | 0 | 0% | 0.090862 | 72297.9483 | 0 | 72297.9483
| C3 | LoadUnload | 125 | 62 | 947 | 0 | 87.4213 | 377.6071 | 721750 | 3117524 | 0.23151 | 3292 | 39.87% | 4964 | 60.13% | 87.4213 | 721750 | 100% | 0 | 0% | 0.090862 | 65579.8215 | 0 | 65579.8215
| C4 | LoadUnload | 177 | 88 | 1326 | 0 | 96.0144 | 112.5879 | 792694.5 | 929526 | 0.85279 | 701 | 8.491% | 7555 | 91.51% | 96.0144 | 792694.5 | 100% | 0 | 0% | 0.090862 | 72025.9976 | 0 | 72025.9976
| C5 | InletModulation | 384 | 0 | 2604 | 0 | 287.6984 | 427.1831 | 2375238.1935 | 3526824 | 0.67348 | 8256 | 100% | 0 | 0% | 287.6984 | 2375238.1935 | 100% | 0 | 0% | 0.090862 | 215819.462 | 0 | 215819.462
| C6 | LoadUnload | 274 | 137 | 1902 | 0 | 220.2355 | 1155.5756 | 1818264 | 9540432 | 0.19059 | 5016 | 60.76% | 3240 | 39.24% | 274 | 1374384 | 75.59% | 443880 | 24.41% | 0.090862 | 124879.6084 | 40331.9309 | 165211.5393
| Total |  | 1210 | 411 | 8673 | 0 | 888.514 | 3166.0872 | 7335571.6935 | 26139216 | 0.28063 | 26795 | 54.09% | 22741 | 45.91% | 888.514 | 6891691.6935 | 93.95% | 443880 | 6.051% | 0.090862 | 626194.5422 | 40331.9309 | 666526.4732

## Control Scheme 4 Graphs
Analysis
| 2018 Actual Power Usage: |  | 3633181.008 | kWh
CS4
| LU+VS Data | Units | Compressors | op1 | op2 | op3 | op4 |  |  | Time Loaded | Time Unloaded | Total |  |  | Time Loaded | Time Unloaded | Total |  |  | Loaded Energy | Unloaded Energy | Total |  |  | Loaded Energy | Unloaded Energy | Total |  |  | Loaded Cost | Unloaded Cost | Total
| Average Power | kW | C1 | 100.7676 | 76.5352 | 76.5352 | 100.7676 | op1 |  |  |  |  | op1 |  |  |  |  | op1 |  |  |  |  | op1 |  |  |  |  | op1
|  | kW | C2 | 96.3769 | 67.7538 | 67.7538 | 96.3769 |  | C1 | 5055 | 3201 | 8256 |  | C1 | 61.23% | 38.77% | 100% |  | C1 | 831937.5 | 0 | 831937.5 |  | C1 | 100% | 0% | 100% |  | C1 | 75591.7045 | 0 | 75591.7045
|  | kW | C3 | 87.4213 | 49.8425 | 49.8425 | 87.4213 |  | C2 | 4475 | 3781 | 8256 |  | C2 | 54.2% | 45.8% | 100% |  | C2 | 795687.5 | 0 | 795687.5 |  | C2 | 100% | 0% | 100% |  | C2 | 72297.9483 | 0 | 72297.9483
|  | kW | C4 | 96.0144 | 15.0287 | 15.0287 | 96.0144 |  | C3 | 3292 | 4964 | 8256 |  | C3 | 39.87% | 60.13% | 100% |  | C3 | 721750 | 0 | 721750 |  | C3 | 100% | 0% | 100% |  | C3 | 65579.8215 | 0 | 65579.8215
|  | kW | C5 | 62.9947 | 62.9947 | 287.6984 | 287.6984 |  | C4 | 701 | 7555 | 8256 |  | C4 | 8.491% | 91.51% | 100% |  | C4 | 792694.5 | 0 | 792694.5 |  | C4 | 100% | 0% | 100% |  | C4 | 72025.9976 | 0 | 72025.9976
|  | kW | C6 | 220.2355 | 166.4709 | 166.4709 | 220.2355 |  | C5 | 6816 | 1440 | 8256 |  | C5 | 82.56% | 17.44% | 100% |  | C5 | 520084.6452 | 0 | 520084.6452 |  | C5 | 100% | 0% | 100% |  | C5 | 47256.0557 | 0 | 47256.0557
|  | kW | Total | 663.8103 | 438.6259 | 663.3296 | 888.514 |  | C6 | 5016 | 3240 | 8256 |  | C6 | 60.76% | 39.24% | 100% |  | C6 | 1374384 | 443880 | 1818264 |  | C6 | 75.59% | 24.41% | 100% |  | C6 | 124879.6084 | 40331.9309 | 165211.5393
| Average Power | % | C1 | 15.18% | 17.45% | 11.54% | 11.34%
|  | % | C2 | 14.52% | 15.45% | 10.21% | 10.85% | op2 |  |  |  |  | op2 |  |  |  |  | op2 |  |  |  |  | op2 |  |  |  |  | op2
|  | % | C3 | 13.17% | 11.36% | 7.514% | 9.839% |  | C1 | 5055 | 3201 | 8256 |  | C1 | 61.23% | 38.77% | 100% |  | C1 | 631875 | 0 | 631875 |  | C1 | 100% | 0% | 100% |  | C1 | 57413.5777 | 0 | 57413.5777
|  | % | C4 | 14.46% | 3.426% | 2.266% | 10.81% |  | C2 | 4475 | 3781 | 8256 |  | C2 | 54.2% | 45.8% | 100% |  | C2 | 559375 | 0 | 559375 |  | C2 | 100% | 0% | 100% |  | C2 | 50826.0653 | 0 | 50826.0653
|  | % | C5 | 9.49% | 14.36% | 43.37% | 32.38% |  | C3 | 3292 | 4964 | 8256 |  | C3 | 39.87% | 60.13% | 100% |  | C3 | 411500 | 0 | 411500 |  | C3 | 100% | 0% | 100% |  | C3 | 37389.8116 | 0 | 37389.8116
|  | % | C6 | 33.18% | 37.95% | 25.1% | 24.79% |  | C4 | 701 | 7555 | 8256 |  | C4 | 8.491% | 91.51% | 100% |  | C4 | 124077 | 0 | 124077 |  | C4 | 100% | 0% | 100% |  | C4 | 11273.9141 | 0 | 11273.9141
|  | % | Total | 100% | 100% | 100% | 100% |  | C5 | 6816 | 1440 | 8256 |  | C5 | 82.56% | 17.44% | 100% |  | C5 | 520084.6452 | 0 | 520084.6452 |  | C5 | 100% | 0% | 100% |  | C5 | 47256.0557 | 0 | 47256.0557
| Average Air Output | m3/hr | C1 | 579.831 | 579.831 | 579.831 | 579.831 |  | C6 | 5016 | 3240 | 8256 |  | C6 | 60.76% | 39.24% | 100% |  | C6 | 1374384 | 0 | 1374384 |  | C6 | 100% | 0% | 100% |  | C6 | 124879.6084 | 0 | 124879.6084
|  | m3/hr | C2 | 513.3024 | 513.3024 | 513.3024 | 513.3024
|  | m3/hr | C3 | 377.6071 | 377.6071 | 377.6071 | 377.6071 | op3 |  |  |  |  | op3 |  |  |  |  | op3 |  |  |  |  | op3 |  |  |  |  | op3
|  | m3/hr | C4 | 112.5879 | 112.5879 | 112.5879 | 112.5879 |  | C1 | 5055 | 3201 | 8256 |  | C1 | 61.23% | 38.77% | 100% |  | C1 | 631875 | 0 | 631875 |  | C1 | 100% | 0% | 100% |  | C1 | 57413.5777 | 0 | 57413.5777
|  | m3/hr | C5 | 427.1831 | 427.1831 | 427.1831 | 427.1831 |  | C2 | 4475 | 3781 | 8256 |  | C2 | 54.2% | 45.8% | 100% |  | C2 | 559375 | 0 | 559375 |  | C2 | 100% | 0% | 100% |  | C2 | 50826.0653 | 0 | 50826.0653
|  | m3/hr | C6 | 1155.5756 | 1155.5756 | 1155.5756 | 1155.5756 |  | C3 | 3292 | 4964 | 8256 |  | C3 | 39.87% | 60.13% | 100% |  | C3 | 411500 | 0 | 411500 |  | C3 | 100% | 0% | 100% |  | C3 | 37389.8116 | 0 | 37389.8116
|  | m3/hr | Total | 3166.0872 | 3166.0872 | 3166.0872 | 3166.0872 |  | C4 | 701 | 7555 | 8256 |  | C4 | 8.491% | 91.51% | 100% |  | C4 | 124077 | 0 | 124077 |  | C4 | 100% | 0% | 100% |  | C4 | 11273.9141 | 0 | 11273.9141
| Average Air Output | % | C1 | 18.31% | 18.31% | 18.31% | 18.31% |  | C5 | 8256 | 0 | 8256 |  | C5 | 100% | 0% | 100% |  | C5 | 2375238.1935 | 0 | 2375238.1935 |  | C5 | 100% | 0% | 100% |  | C5 | 215819.462 | 0 | 215819.462
|  | % | C2 | 16.21% | 16.21% | 16.21% | 16.21% |  | C6 | 5016 | 3240 | 8256 |  | C6 | 60.76% | 39.24% | 100% |  | C6 | 1374384 | 0 | 1374384 |  | C6 | 100% | 0% | 100% |  | C6 | 124879.6084 | 0 | 124879.6084
|  | % | C3 | 11.93% | 11.93% | 11.93% | 11.93%
|  | % | C4 | 3.556% | 3.556% | 3.556% | 3.556% | op4 |  |  |  |  | op4 |  |  |  |  | op4 |  |  |  |  | op4 |  |  |  |  | op4
|  | % | C5 | 13.49% | 13.49% | 13.49% | 13.49% |  | C1 | 5055 | 3201 | 8256 |  | C1 | 61.23% | 38.77% | 100% |  | C1 | 831937.5 | 0 | 831937.5 |  | C1 | 100% | 0% | 100% |  | C1 | 75591.7045 | 0 | 75591.7045
|  | % | C6 | 36.5% | 36.5% | 36.5% | 36.5% |  | C2 | 4475 | 3781 | 8256 |  | C2 | 54.2% | 45.8% | 100% |  | C2 | 795687.5 | 0 | 795687.5 |  | C2 | 100% | 0% | 100% |  | C2 | 72297.9483 | 0 | 72297.9483
|  | % | Total | 100% | 100% | 100% | 100% |  | C3 | 3292 | 4964 | 8256 |  | C3 | 39.87% | 60.13% | 100% |  | C3 | 721750 | 0 | 721750 |  | C3 | 100% | 0% | 100% |  | C3 | 65579.8215 | 0 | 65579.8215
| Total Energy | kWh | C1 | 831937.5 | 631875 | 631875 | 831937.5 |  | C4 | 701 | 7555 | 8256 |  | C4 | 8.491% | 91.51% | 100% |  | C4 | 792694.5 | 0 | 792694.5 |  | C4 | 100% | 0% | 100% |  | C4 | 72025.9976 | 0 | 72025.9976
|  | kWh | C2 | 795687.5 | 559375 | 559375 | 795687.5 |  | C5 | 8256 | 0 | 8256 |  | C5 | 100% | 0% | 100% |  | C5 | 2375238.1935 | 0 | 2375238.1935 |  | C5 | 100% | 0% | 100% |  | C5 | 215819.462 | 0 | 215819.462
|  | kWh | C3 | 721750 | 411500 | 411500 | 721750 |  | C6 | 5016 | 3240 | 8256 |  | C6 | 60.76% | 39.24% | 100% |  | C6 | 1374384 | 443880 | 1818264 |  | C6 | 75.59% | 24.41% | 100% |  | C6 | 124879.6084 | 40331.9309 | 165211.5393
|  | kWh | C4 | 792694.5 | 124077 | 124077 | 792694.5
|  | kWh | C5 | 520084.6452 | 520084.6452 | 2375238.1935 | 2375238.1935
|  | kWh | C6 | 1818264 | 1374384 | 1374384 | 1818264
|  | kWh | Total | 5480418.1452 | 3621295.6452 | 5476449.1935 | 7335571.6935
| Total Energy | % | C1 | 15.18% | 17.45% | 11.54% | 11.34%
|  | % | C2 | 14.52% | 15.45% | 10.21% | 10.85%
|  | % | C3 | 13.17% | 11.36% | 7.514% | 9.839%
|  | % | C4 | 14.46% | 3.426% | 2.266% | 10.81%
|  | % | C5 | 9.49% | 14.36% | 43.37% | 32.38%
|  | % | C6 | 33.18% | 37.95% | 25.1% | 24.79%
|  | % | Total | 100% | 100% | 100% | 100%
| Total Air Output | m3/hr | C1 | 4787085 | 4787085 | 4787085 | 4787085
|  | m3/hr | C2 | 4237825 | 4237825 | 4237825 | 4237825
|  | m3/hr | C3 | 3117524 | 3117524 | 3117524 | 3117524
|  | m3/hr | C4 | 929526 | 929526 | 929526 | 929526
|  | m3/hr | C5 | 3526824 | 3526824 | 3526824 | 3526824
|  | m3/hr | C6 | 9540432 | 9540432 | 9540432 | 9540432
|  | m3/hr | Total | 26139216 | 26139216 | 26139216 | 26139216
| Total Air Output | % | C1 | 18.31% | 18.31% | 18.31% | 18.31%
|  | % | C2 | 16.21% | 16.21% | 16.21% | 16.21%
|  | % | C3 | 11.93% | 11.93% | 11.93% | 11.93%
|  | % | C4 | 3.556% | 3.556% | 3.556% | 3.556%
|  | % | C5 | 13.49% | 13.49% | 13.49% | 13.49%
|  | % | C6 | 36.5% | 36.5% | 36.5% | 36.5%
|  | % | Total | 100% | 100% | 100% | 100%
| Average Efficiency | kW/m3/hr | C1 | 0.17379 | 0.132 | 0.132 | 0.17379
|  | kW/m3/hr | C2 | 0.18776 | 0.132 | 0.132 | 0.18776
|  | kW/m3/hr | C3 | 0.23151 | 0.132 | 0.132 | 0.23151
|  | kW/m3/hr | C4 | 0.85279 | 0.13348 | 0.13348 | 0.85279
|  | kW/m3/hr | C5 | 0.14747 | 0.14747 | 0.67348 | 0.67348
|  | kW/m3/hr | C6 | 0.19059 | 0.14406 | 0.14406 | 0.19059
|  | kW/m3/hr | Total | 0.20966 | 0.13854 | 0.20951 | 0.28063
| Time Loaded | hrs | C1 | 5055 | 5055 | 5055 | 5055
|  | hrs | C2 | 4475 | 4475 | 4475 | 4475
|  | hrs | C3 | 3292 | 3292 | 3292 | 3292
|  | hrs | C4 | 701 | 701 | 701 | 701
|  | hrs | C5 | 6816 | 6816 | 8256 | 8256
|  | hrs | C6 | 5016 | 5016 | 5016 | 5016
|  | hrs | Total | 25355 | 25355 | 26795 | 26795
| Time Loaded | % | C1 | 61.23% | 61.23% | 61.23% | 61.23%
|  | % | C2 | 54.2% | 54.2% | 54.2% | 54.2%
|  | % | C3 | 39.87% | 39.87% | 39.87% | 39.87%
|  | % | C4 | 8.491% | 8.491% | 8.491% | 8.491%
|  | % | C5 | 82.56% | 82.56% | 100% | 100%
|  | % | C6 | 60.76% | 60.76% | 60.76% | 60.76%
|  | % | Total | 51.18% | 51.18% | 54.09% | 54.09%
| Time Unloaded | hrs | C1 | 3201 | 3201 | 3201 | 3201
|  | hrs | C2 | 3781 | 3781 | 3781 | 3781
|  | hrs | C3 | 4964 | 4964 | 4964 | 4964
|  | hrs | C4 | 7555 | 7555 | 7555 | 7555
|  | hrs | C5 | 1440 | 1440 | 0 | 0
|  | hrs | C6 | 3240 | 3240 | 3240 | 3240
|  | hrs | Total | 24181 | 24181 | 22741 | 22741
| Time Unloaded | % | C1 | 38.77% | 38.77% | 38.77% | 38.77%
|  | % | C2 | 45.8% | 45.8% | 45.8% | 45.8%
|  | % | C3 | 60.13% | 60.13% | 60.13% | 60.13%
|  | % | C4 | 91.51% | 91.51% | 91.51% | 91.51%
|  | % | C5 | 17.44% | 17.44% | 0% | 0%
|  | % | C6 | 39.24% | 39.24% | 39.24% | 39.24%
|  | % | Total | 48.82% | 48.82% | 45.91% | 45.91%
| Total Time | hrs | C1 | 8256 | 8256 | 8256 | 8256
|  | hrs | C2 | 8256 | 8256 | 8256 | 8256
|  | hrs | C3 | 8256 | 8256 | 8256 | 8256
|  | hrs | C4 | 8256 | 8256 | 8256 | 8256
|  | hrs | C5 | 8256 | 8256 | 8256 | 8256
|  | hrs | C6 | 8256 | 8256 | 8256 | 8256
|  | hrs | Total | 49536 | 49536 | 49536 | 49536
| Loaded Energy | kWh | C1 | 831937.5 | 631875 | 631875 | 831937.5
|  | kWh | C2 | 795687.5 | 559375 | 559375 | 795687.5
|  | kWh | C3 | 721750 | 411500 | 411500 | 721750
|  | kWh | C4 | 792694.5 | 124077 | 124077 | 792694.5
|  | kWh | C5 | 520084.6452 | 520084.6452 | 2375238.1935 | 2375238.1935
|  | kWh | C6 | 1374384 | 1374384 | 1374384 | 1374384
|  | kWh | Total | 5036538.1452 | 3621295.6452 | 5476449.1935 | 6891691.6935
| Loaded Energy | % | C1 | 100% | 100% | 100% | 100%
|  | % | C2 | 100% | 100% | 100% | 100%
|  | % | C3 | 100% | 100% | 100% | 100%
|  | % | C4 | 100% | 100% | 100% | 100%
|  | % | C5 | 100% | 100% | 100% | 100%
|  | % | C6 | 75.59% | 100% | 100% | 75.59%
|  | % | Total | 91.9% | 100% | 100% | 93.95%
| Unloaded Energy | kWh | C1 | 0 | 0 | 0 | 0
|  | kWh | C2 | 0 | 0 | 0 | 0
|  | kWh | C3 | 0 | 0 | 0 | 0
|  | kWh | C4 | 0 | 0 | 0 | 0
|  | kWh | C5 | 0 | 0 | 0 | 0
|  | kWh | C6 | 443880 | 0 | 0 | 443880
|  | kWh | Total | 443880 | 0 | 0 | 443880
| Unloaded Energy | % | C1 | 0% | 0% | 0% | 0%
|  | % | C2 | 0% | 0% | 0% | 0%
|  | % | C3 | 0% | 0% | 0% | 0%
|  | % | C4 | 0% | 0% | 0% | 0%
|  | % | C5 | 0% | 0% | 0% | 0%
|  | % | C6 | 24.41% | 0% | 0% | 24.41%
|  | % | Total | 8.099% | 0% | 0% | 6.051%
| Total Energy | kWh | C1 | 831937.5 | 631875 | 631875 | 831937.5
|  | kWh | C2 | 795687.5 | 559375 | 559375 | 795687.5
|  | kWh | C3 | 721750 | 411500 | 411500 | 721750
|  | kWh | C4 | 792694.5 | 124077 | 124077 | 792694.5
|  | kWh | C5 | 520084.6452 | 520084.6452 | 2375238.1935 | 2375238.1935
|  | kWh | C6 | 1818264 | 1374384 | 1374384 | 1818264
|  | kWh | Total | 5480418.1452 | 3621295.6452 | 5476449.1935 | 7335571.6935
| Loaded Cost | £ | C1 | 75591.7045 | 57413.5777 | 57413.5777 | 75591.7045
|  | £ | C2 | 72297.9483 | 50826.0653 | 50826.0653 | 72297.9483
|  | £ | C3 | 65579.8215 | 37389.8116 | 37389.8116 | 65579.8215
|  | £ | C4 | 72025.9976 | 11273.9141 | 11273.9141 | 72025.9976
|  | £ | C5 | 47256.0557 | 47256.0557 | 215819.462 | 215819.462
|  | £ | C6 | 124879.6084 | 124879.6084 | 124879.6084 | 124879.6084
|  | £ | Total | 457631.1359 | 329039.0327 | 497602.439 | 626194.5422
| Unloaded Cost | £ | C1 | 0 | 0 | 0 | 0
|  | £ | C2 | 0 | 0 | 0 | 0
|  | £ | C3 | 0 | 0 | 0 | 0
|  | £ | C4 | 0 | 0 | 0 | 0
|  | £ | C5 | 0 | 0 | 0 | 0
|  | £ | C6 | 40331.9309 | 0 | 0 | 40331.9309
|  | £ | Total | 40331.9309 | 0 | 0 | 40331.9309
| Total Cost | £ | C1 | 75591.7045 | 58151.8334 | 57413.5777 | 75591.7045
|  | £ | C2 | 72297.9483 | 55902.9929 | 50826.0653 | 72297.9483
|  | £ | C3 | 65579.8215 | 47327.8691 | 37389.8116 | 65579.8215
|  | £ | C4 | 72025.9976 | 79657.1991 | 11273.9141 | 72025.9976
|  | £ | C5 | 47256.0557 | 64078.4029 | 215819.462 | 215819.462
|  | £ | C6 | 165211.5393 | 17452.2738 | 124879.6084 | 165211.5393
|  | £ | Total | 497963.0669 | 322570.5713 | 497602.439 | 666526.4732

## All Control Schemes Graphs
Analysis
| 2018 Actual Power Usage: |  | 3633181.008 | kWh
|  |  |  | Opt |  |  |  | CS1 |  |  |  | CS2 |  |  |  | CS3 |  |  |  | CS4
|  |  |  | op1 op2 op3 op4 |  |  |  | op1 op2 op3 op4 |  |  |  | op1 op2 op3 op4 |  |  |  | op1 op2 op3 op4 |  |  |  | op1 op2 op3 op4
|  |  |  | Opt |  |  |  | CS1 |  |  |  | CS2 |  |  |  | CS3 |  |  |  | CS4
| LU+VS Data | Units | Compressors | op1 | op2 | op3 | op4 | op1 | op2 | op3 | op4 | op1 | op2 | op3 | op4 | op1 | op2 | op3 | op4 | op1 | op2 | op3 | op4 |  |  | Time Loaded | Time Unloaded | Total |  |  | Time Loaded | Time Unloaded | Total |  |  | Loaded Energy | Unloaded Energy | Total |  |  | Loaded Energy | Unloaded Energy | Total |  |  | Loaded Cost | Unloaded Cost | Total
| Average Power | kW | C1 | 101.2597 | 77.5194 | 69.7069 | 97.467 | 101.8956 | 78.7912 | 78.7912 | 101.8956 | 101.2597 | 77.5194 | 77.5194 | 101.2597 | 100.7676 | 76.5352 | 76.5352 | 100.7676 | 100.7676 | 76.5352 | 76.5352 | 100.7676 | op1 |  |  |  |  | op1 |  |  |  |  | op1 |  |  |  |  | op1 |  |  |  |  | op1
|  | kW | C2 | 99.7608 | 74.5216 | 56.5801 | 90.9339 | 100.4875 | 75.975 | 75.975 | 100.4875 | 99.7608 | 74.5216 | 74.5216 | 99.7608 | 96.3769 | 67.7538 | 67.7538 | 96.3769 | 96.3769 | 67.7538 | 67.7538 | 96.3769 |  | C1 | 5120 | 3136 | 8256 |  | C1 | 62.02% | 37.98% | 100% |  | C1 | 836000 | 0 | 836000 |  | C1 | 100% | 0% | 100% |  | C1 | 75960.8323 | 0 | 75960.8323
|  | kW | C3 | 79.3211 | 63.0753 | 20.0309 | 80.169 | 99.3444 | 73.6888 | 73.6888 | 99.3444 | 94.0452 | 63.0905 | 63.0905 | 94.0452 | 87.4213 | 49.8425 | 49.8425 | 87.4213 | 87.4213 | 49.8425 | 49.8425 | 87.4213 |  | C2 | 4922 | 3334 | 8256 |  | C2 | 59.62% | 40.38% | 100% |  | C2 | 823625 | 0 | 823625 |  | C2 | 100% | 0% | 100% |  | C2 | 74836.4121 | 0 | 74836.4121
|  | kW | C4 | 130.381 | 106.23 | 38.8259 | 119.1148 | 104.3863 | 31.7725 | 31.7725 | 104.3863 | 141.5936 | 106.1871 | 106.1871 | 141.5936 | 96.0144 | 15.0287 | 15.0287 | 96.0144 | 96.0144 | 15.0287 | 15.0287 | 96.0144 |  | C3 | 2222 | 6034 | 8256 |  | C3 | 26.91% | 73.09% | 100% |  | C3 | 654875 | 0 | 654875 |  | C3 | 100% | 0% | 100% |  | C3 | 59503.4092 | 0 | 59503.4092
|  | kW | C5 | 41.0386 | 84.9763 | 66.5596 | 65.2557 | 64.7201 | 64.7201 | 288.216 | 288.216 | 85.4198 | 85.4198 | 294.4259 | 294.4259 | 62.9947 | 62.9947 | 287.6984 | 287.6984 | 62.9947 | 62.9947 | 287.6984 | 287.6984 |  | C4 | 3907 | 4349 | 8256 |  | C4 | 47.32% | 52.68% | 100% |  | C4 | 1076425.5 | 0 | 1076425.5 |  | C4 | 100% | 0% | 100% |  | C4 | 97806.4317 | 0 | 97806.4317
|  | kW | C6 | 198.2816 | 23.2648 | 36.4404 | 137.8795 | 191.6274 | 109.2548 | 109.2548 | 191.6274 | 148.6324 | 23.2648 | 23.2648 | 148.6324 | 220.2355 | 166.4709 | 166.4709 | 220.2355 | 220.2355 | 166.4709 | 166.4709 | 220.2355 |  | C5 | 6720 | 1536 | 8256 |  | C5 | 81.4% | 18.6% | 100% |  | C5 | 338815 | 0 | 338815 |  | C5 | 100% | 0% | 100% |  | C5 | 30785.4897 | 0 | 30785.4897
|  | kW | Total | 650.0428 | 429.5873 | 288.1438 | 590.8199 | 662.4613 | 434.2025 | 657.6985 | 885.9572 | 670.7115 | 430.0031 | 639.0093 | 879.7176 | 663.8103 | 438.6259 | 663.3296 | 888.514 | 663.8103 | 438.6259 | 663.3296 | 888.514 |  | C6 | 3693 | 4563 | 8256 |  | C6 | 44.73% | 55.27% | 100% |  | C6 | 1011882 | 625131 | 1637013 |  | C6 | 61.81% | 38.19% | 100% |  | C6 | 91941.8648 | 56800.8027 | 148742.6675
| Average Power | % | C1 | 15.58% | 18.05% | 24.19% | 16.5% | 15.38% | 18.15% | 11.98% | 11.5% | 15.1% | 18.03% | 12.13% | 11.51% | 15.18% | 17.45% | 11.54% | 11.34% | 15.18% | 17.45% | 11.54% | 11.34%
|  | % | C2 | 15.35% | 17.35% | 19.64% | 15.39% | 15.17% | 17.5% | 11.55% | 11.34% | 14.87% | 17.33% | 11.66% | 11.34% | 14.52% | 15.45% | 10.21% | 10.85% | 14.52% | 15.45% | 10.21% | 10.85% | op2 |  |  |  |  | op2 |  |  |  |  | op2 |  |  |  |  | op2 |  |  |  |  | op2
|  | % | C3 | 12.2% | 14.68% | 6.952% | 13.57% | 15% | 16.97% | 11.2% | 11.21% | 14.02% | 14.67% | 9.873% | 10.69% | 13.17% | 11.36% | 7.514% | 9.839% | 13.17% | 11.36% | 7.514% | 9.839% |  | C1 | 5120 | 3136 | 8256 |  | C1 | 62.02% | 37.98% | 100% |  | C1 | 640000 | 0 | 640000 |  | C1 | 100% | 0% | 100% |  | C1 | 58151.8334 | 0 | 58151.8334
|  | % | C4 | 20.06% | 24.73% | 13.47% | 20.16% | 15.76% | 7.317% | 4.831% | 11.78% | 21.11% | 24.69% | 16.62% | 16.1% | 14.46% | 3.426% | 2.266% | 10.81% | 14.46% | 3.426% | 2.266% | 10.81% |  | C2 | 4922 | 3334 | 8256 |  | C2 | 59.62% | 40.38% | 100% |  | C2 | 615250 | 0 | 615250 |  | C2 | 100% | 0% | 100% |  | C2 | 55902.9929 | 0 | 55902.9929
|  | % | C5 | 6.313% | 19.78% | 23.1% | 11.04% | 9.77% | 14.91% | 43.82% | 32.53% | 12.74% | 19.86% | 46.08% | 33.47% | 9.49% | 14.36% | 43.37% | 32.38% | 9.49% | 14.36% | 43.37% | 32.38% |  | C3 | 4166 | 4090 | 8256 |  | C3 | 50.46% | 49.54% | 100% |  | C3 | 520750 | 0 | 520750 |  | C3 | 100% | 0% | 100% |  | C3 | 47316.5113 | 0 | 47316.5113
|  | % | C6 | 30.5% | 5.416% | 12.65% | 23.34% | 28.93% | 25.16% | 16.61% | 21.63% | 22.16% | 5.41% | 3.641% | 16.9% | 33.18% | 37.95% | 25.1% | 24.79% | 33.18% | 37.95% | 25.1% | 24.79% |  | C4 | 4955 | 3301 | 8256 |  | C4 | 60.02% | 39.98% | 100% |  | C4 | 877035 | 0 | 877035 |  | C4 | 100% | 0% | 100% |  | C4 | 79689.3643 | 0 | 79689.3643
|  | % | Total | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% |  | C5 | 6755 | 1501 | 8256 |  | C5 | 81.82% | 18.18% | 100% |  | C5 | 701564 | 0 | 701564 |  | C5 | 100% | 0% | 100% |  | C5 | 63745.6763 | 0 | 63745.6763
| Average Air Output | m3/hr | C1 | 587.2868 | 587.2868 | 528.0993 | 529.8199 | 596.922 | 596.922 | 596.922 | 596.922 | 587.2868 | 587.2868 | 587.2868 | 587.2868 | 579.831 | 579.831 | 579.831 | 579.831 | 579.831 | 579.831 | 579.831 | 579.831 |  | C6 | 701 | 7555 | 8256 |  | C6 | 8.491% | 91.51% | 100% |  | C6 | 192074 | 0 | 192074 |  | C6 | 100% | 0% | 100% |  | C6 | 17452.2738 | 0 | 17452.2738
|  | m3/hr | C2 | 564.5753 | 564.5753 | 428.6506 | 430.8299 | 575.587 | 575.587 | 575.587 | 575.587 | 564.5753 | 564.5753 | 564.5753 | 564.5753 | 513.3024 | 513.3024 | 513.3024 | 513.3024 | 513.3024 | 513.3024 | 513.3024 | 513.3024
|  | m3/hr | C3 | 254.8733 | 477.8588 | 151.754 | 267.7202 | 558.2666 | 558.2666 | 558.2666 | 558.2666 | 477.9735 | 477.9735 | 477.9735 | 477.9735 | 377.6071 | 377.6071 | 377.6071 | 377.6071 | 377.6071 | 377.6071 | 377.6071 | 377.6071 | op3 |  |  |  |  | op3 |  |  |  |  | op3 |  |  |  |  | op3 |  |  |  |  | op3
|  | m3/hr | C4 | 627.5051 | 795.8249 | 290.8656 | 458.7035 | 238.0247 | 238.0247 | 238.0247 | 238.0247 | 795.5036 | 795.5036 | 795.5036 | 795.5036 | 112.5879 | 112.5879 | 112.5879 | 112.5879 | 112.5879 | 112.5879 | 112.5879 | 112.5879 |  | C1 | 4604 | 3652 | 8256 |  | C1 | 55.77% | 44.23% | 100% |  | C1 | 575500 | 0 | 575500 |  | C1 | 100% | 0% | 100% |  | C1 | 52291.2189 | 0 | 52291.2189
|  | m3/hr | C5 | 281.061 | 579.0465 | 1513.7628 | 1466.8037 | 438.8829 | 438.8829 | 438.8829 | 438.8829 | 579.253 | 579.253 | 579.253 | 579.253 | 427.1831 | 427.1831 | 427.1831 | 427.1831 | 427.1831 | 427.1831 | 427.1831 | 427.1831 |  | C2 | 3737 | 4519 | 8256 |  | C2 | 45.26% | 54.74% | 100% |  | C2 | 467125 | 0 | 467125 |  | C2 | 100% | 0% | 100% |  | C2 | 42444.0237 | 0 | 42444.0237
|  | m3/hr | C6 | 850.7856 | 161.4949 | 252.9549 | 12.21 | 758.4041 | 758.4041 | 758.4041 | 758.4041 | 161.4949 | 161.4949 | 161.4949 | 161.4949 | 1155.5756 | 1155.5756 | 1155.5756 | 1155.5756 | 1155.5756 | 1155.5756 | 1155.5756 | 1155.5756 |  | C3 | 1323 | 6933 | 8256 |  | C3 | 16.02% | 83.98% | 100% |  | C3 | 165375 | 0 | 165375 |  | C3 | 100% | 0% | 100% |  | C3 | 15026.3429 | 0 | 15026.3429
|  | m3/hr | Total | 3166.0872 | 3166.0872 | 3166.0872 | 3166.0872 | 3166.0872 | 3166.0872 | 3166.0872 | 3166.0872 | 3166.0872 | 3166.0872 | 3166.0872 | 3166.0872 | 3166.0872 | 3166.0872 | 3166.0872 | 3166.0872 | 3166.0872 | 3166.0872 | 3166.0872 | 3166.0872 |  | C4 | 1811 | 6445 | 8256 |  | C4 | 21.94% | 78.06% | 100% |  | C4 | 320547 | 0 | 320547 |  | C4 | 100% | 0% | 100% |  | C4 | 29125.6183 | 0 | 29125.6183
| Average Air Output | % | C1 | 18.55% | 18.55% | 16.68% | 16.73% | 18.85% | 18.85% | 18.85% | 18.85% | 18.55% | 18.55% | 18.55% | 18.55% | 18.31% | 18.31% | 18.31% | 18.31% | 18.31% | 18.31% | 18.31% | 18.31% |  | C5 | 6742 | 1514 | 8256 |  | C5 | 81.66% | 18.34% | 100% |  | C5 | 549516 | 0 | 549516 |  | C5 | 100% | 0% | 100% |  | C5 | 49930.2545 | 0 | 49930.2545
|  | % | C2 | 17.83% | 17.83% | 13.54% | 13.61% | 18.18% | 18.18% | 18.18% | 18.18% | 17.83% | 17.83% | 17.83% | 17.83% | 16.21% | 16.21% | 16.21% | 16.21% | 16.21% | 16.21% | 16.21% | 16.21% |  | C6 | 1098 | 7158 | 8256 |  | C6 | 13.3% | 86.7% | 100% |  | C6 | 300852 | 0 | 300852 |  | C6 | 100% | 0% | 100% |  | C6 | 27336.0865 | 0 | 27336.0865
|  | % | C3 | 8.05% | 15.09% | 4.793% | 8.456% | 17.63% | 17.63% | 17.63% | 17.63% | 15.1% | 15.1% | 15.1% | 15.1% | 11.93% | 11.93% | 11.93% | 11.93% | 11.93% | 11.93% | 11.93% | 11.93%
|  | % | C4 | 19.82% | 25.14% | 9.187% | 14.49% | 7.518% | 7.518% | 7.518% | 7.518% | 25.13% | 25.13% | 25.13% | 25.13% | 3.556% | 3.556% | 3.556% | 3.556% | 3.556% | 3.556% | 3.556% | 3.556% | op4 |  |  |  |  | op4 |  |  |  |  | op4 |  |  |  |  | op4 |  |  |  |  | op4
|  | % | C5 | 8.877% | 18.29% | 47.81% | 46.33% | 13.86% | 13.86% | 13.86% | 13.86% | 18.3% | 18.3% | 18.3% | 18.3% | 13.49% | 13.49% | 13.49% | 13.49% | 13.49% | 13.49% | 13.49% | 13.49% |  | C1 | 4619 | 3637 | 8256 |  | C1 | 55.95% | 44.05% | 100% |  | C1 | 804687.5 | 0 | 804687.5 |  | C1 | 100% | 0% | 100% |  | C1 | 73115.7085 | 0 | 73115.7085
|  | % | C6 | 26.87% | 5.101% | 7.99% | 0.3857% | 23.95% | 23.95% | 23.95% | 23.95% | 5.101% | 5.101% | 5.101% | 5.101% | 36.5% | 36.5% | 36.5% | 36.5% | 36.5% | 36.5% | 36.5% | 36.5% |  | C2 | 3756 | 4500 | 8256 |  | C2 | 45.49% | 54.51% | 100% |  | C2 | 750750 | 0 | 750750 |  | C2 | 100% | 0% | 100% |  | C2 | 68214.8264 | 0 | 68214.8264
|  | % | Total | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% |  | C3 | 2334 | 5922 | 8256 |  | C3 | 28.27% | 71.73% | 100% |  | C3 | 661875 | 0 | 661875 |  | C3 | 100% | 0% | 100% |  | C3 | 60139.4449 | 0 | 60139.4449
| Total Energy | kWh | C1 | 836000 | 640000 | 575500 | 804687.5 | 841250 | 650500 | 650500 | 841250 | 836000 | 640000 | 640000 | 836000 | 831937.5 | 631875 | 631875 | 831937.5 | 831937.5 | 631875 | 631875 | 831937.5 |  | C4 | 2856 | 5400 | 8256 |  | C4 | 34.59% | 65.41% | 100% |  | C4 | 983412 | 0 | 983412 |  | C4 | 100% | 0% | 100% |  | C4 | 89355.0168 | 0 | 89355.0168
|  | kWh | C2 | 823625 | 615250 | 467125 | 750750 | 829625 | 627250 | 627250 | 829625 | 823625 | 615250 | 615250 | 823625 | 795687.5 | 559375 | 559375 | 795687.5 | 795687.5 | 559375 | 559375 | 795687.5 |  | C5 | 6766 | 1490 | 8256 |  | C5 | 81.95% | 18.05% | 100% |  | C5 | 538751.2 | 0 | 538751.2 |  | C5 | 100% | 0% | 100% |  | C5 | 48952.1406 | 0 | 48952.1406
|  | kWh | C3 | 654875 | 520750 | 165375 | 661875 | 820187.5 | 608375 | 608375 | 820187.5 | 776437.5 | 520875 | 520875 | 776437.5 | 721750 | 411500 | 411500 | 721750 | 721750 | 411500 | 411500 | 721750 |  | C6 | 53 | 8203 | 8256 |  | C6 | 0.642% | 99.36% | 100% |  | C6 | 14522 | 1123811 | 1138333 |  | C6 | 1.276% | 98.72% | 100% |  | C6 | 1319.5014 | 102111.9844 | 103431.4858
|  | kWh | C4 | 1076425.5 | 877035 | 320547 | 983412 | 861813 | 262314 | 262314 | 861813 | 1168996.5 | 876681 | 876681 | 1168996.5 | 792694.5 | 124077 | 124077 | 792694.5 | 792694.5 | 124077 | 124077 | 792694.5
|  | kWh | C5 | 338815 | 701564 | 549516 | 538751.2 | 534328.7742 | 534328.7742 | 2379511.4323 | 2379511.4323 | 705225.8802 | 705225.8802 | 2430780.5641 | 2430780.5641 | 520084.6452 | 520084.6452 | 2375238.1935 | 2375238.1935 | 520084.6452 | 520084.6452 | 2375238.1935 | 2375238.1935
|  | kWh | C6 | 1637013 | 192074 | 300852 | 1138333 | 1582076 | 902008 | 902008 | 1582076 | 1227109 | 192074 | 192074 | 1227109 | 1818264 | 1374384 | 1374384 | 1818264 | 1818264 | 1374384 | 1374384 | 1818264
|  | kWh | Total | 5366753.5 | 3546673 | 2378915 | 4877808.7 | 5469280.2742 | 3584775.7742 | 5429958.4323 | 7314462.9323 | 5537393.8802 | 3550105.8802 | 5275660.5641 | 7262948.5641 | 5480418.1452 | 3621295.6452 | 5476449.1935 | 7335571.6935 | 5480418.1452 | 3621295.6452 | 5476449.1935 | 7335571.6935
| Total Energy | % | C1 | 15.58% | 18.05% | 24.19% | 16.5% | 15.38% | 18.15% | 11.98% | 11.5% | 15.1% | 18.03% | 12.13% | 11.51% | 15.18% | 17.45% | 11.54% | 11.34% | 15.18% | 17.45% | 11.54% | 11.34%
|  | % | C2 | 15.35% | 17.35% | 19.64% | 15.39% | 15.17% | 17.5% | 11.55% | 11.34% | 14.87% | 17.33% | 11.66% | 11.34% | 14.52% | 15.45% | 10.21% | 10.85% | 14.52% | 15.45% | 10.21% | 10.85%
|  | % | C3 | 12.2% | 14.68% | 6.952% | 13.57% | 15% | 16.97% | 11.2% | 11.21% | 14.02% | 14.67% | 9.873% | 10.69% | 13.17% | 11.36% | 7.514% | 9.839% | 13.17% | 11.36% | 7.514% | 9.839%
|  | % | C4 | 20.06% | 24.73% | 13.47% | 20.16% | 15.76% | 7.317% | 4.831% | 11.78% | 21.11% | 24.69% | 16.62% | 16.1% | 14.46% | 3.426% | 2.266% | 10.81% | 14.46% | 3.426% | 2.266% | 10.81%
|  | % | C5 | 6.313% | 19.78% | 23.1% | 11.04% | 9.77% | 14.91% | 43.82% | 32.53% | 12.74% | 19.86% | 46.08% | 33.47% | 9.49% | 14.36% | 43.37% | 32.38% | 9.49% | 14.36% | 43.37% | 32.38%
|  | % | C6 | 30.5% | 5.416% | 12.65% | 23.34% | 28.93% | 25.16% | 16.61% | 21.63% | 22.16% | 5.41% | 3.641% | 16.9% | 33.18% | 37.95% | 25.1% | 24.79% | 33.18% | 37.95% | 25.1% | 24.79%
|  | % | Total | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100%
| Total Air Output | m3/hr | C1 | 4848640 | 4848640 | 4359988 | 4374193 | 4928188 | 4928188 | 4928188 | 4928188 | 4848640 | 4848640 | 4848640 | 4848640 | 4787085 | 4787085 | 4787085 | 4787085 | 4787085 | 4787085 | 4787085 | 4787085
|  | m3/hr | C2 | 4661134 | 4661134 | 3538939 | 3556932 | 4752046 | 4752046 | 4752046 | 4752046 | 4661134 | 4661134 | 4661134 | 4661134 | 4237825 | 4237825 | 4237825 | 4237825 | 4237825 | 4237825 | 4237825 | 4237825
|  | m3/hr | C3 | 2104234 | 3945202 | 1252881 | 2210298 | 4609049 | 4609049 | 4609049 | 4609049 | 3946149 | 3946149 | 3946149 | 3946149 | 3117524 | 3117524 | 3117524 | 3117524 | 3117524 | 3117524 | 3117524 | 3117524
|  | m3/hr | C4 | 5180682 | 6570330 | 2401386 | 3787056 | 1965132 | 1965132 | 1965132 | 1965132 | 6567678 | 6567678 | 6567678 | 6567678 | 929526 | 929526 | 929526 | 929526 | 929526 | 929526 | 929526 | 929526
|  | m3/hr | C5 | 2320440 | 4780608 | 12497626 | 12109931 | 3623417 | 3623417 | 3623417 | 3623417 | 4782313 | 4782313 | 4782313 | 4782313 | 3526824 | 3526824 | 3526824 | 3526824 | 3526824 | 3526824 | 3526824 | 3526824
|  | m3/hr | C6 | 7024086 | 1333302 | 2088396 | 100806 | 6261384 | 6261384 | 6261384 | 6261384 | 1333302 | 1333302 | 1333302 | 1333302 | 9540432 | 9540432 | 9540432 | 9540432 | 9540432 | 9540432 | 9540432 | 9540432
|  | m3/hr | Total | 26139216 | 26139216 | 26139216 | 26139216 | 26139216 | 26139216 | 26139216 | 26139216 | 26139216 | 26139216 | 26139216 | 26139216 | 26139216 | 26139216 | 26139216 | 26139216 | 26139216 | 26139216 | 26139216 | 26139216
| Total Air Output | % | C1 | 18.55% | 18.55% | 16.68% | 16.73% | 18.85% | 18.85% | 18.85% | 18.85% | 18.55% | 18.55% | 18.55% | 18.55% | 18.31% | 18.31% | 18.31% | 18.31% | 18.31% | 18.31% | 18.31% | 18.31%
|  | % | C2 | 17.83% | 17.83% | 13.54% | 13.61% | 18.18% | 18.18% | 18.18% | 18.18% | 17.83% | 17.83% | 17.83% | 17.83% | 16.21% | 16.21% | 16.21% | 16.21% | 16.21% | 16.21% | 16.21% | 16.21%
|  | % | C3 | 8.05% | 15.09% | 4.793% | 8.456% | 17.63% | 17.63% | 17.63% | 17.63% | 15.1% | 15.1% | 15.1% | 15.1% | 11.93% | 11.93% | 11.93% | 11.93% | 11.93% | 11.93% | 11.93% | 11.93%
|  | % | C4 | 19.82% | 25.14% | 9.187% | 14.49% | 7.518% | 7.518% | 7.518% | 7.518% | 25.13% | 25.13% | 25.13% | 25.13% | 3.556% | 3.556% | 3.556% | 3.556% | 3.556% | 3.556% | 3.556% | 3.556%
|  | % | C5 | 8.877% | 18.29% | 47.81% | 46.33% | 13.86% | 13.86% | 13.86% | 13.86% | 18.3% | 18.3% | 18.3% | 18.3% | 13.49% | 13.49% | 13.49% | 13.49% | 13.49% | 13.49% | 13.49% | 13.49%
|  | % | C6 | 26.87% | 5.101% | 7.99% | 0.3857% | 23.95% | 23.95% | 23.95% | 23.95% | 5.101% | 5.101% | 5.101% | 5.101% | 36.5% | 36.5% | 36.5% | 36.5% | 36.5% | 36.5% | 36.5% | 36.5%
|  | % | Total | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100%
| Average Efficiency | kW/m3/hr | C1 | 0.17242 | 0.132 | 0.132 | 0.18396 | 0.1707 | 0.132 | 0.132 | 0.1707 | 0.17242 | 0.132 | 0.132 | 0.17242 | 0.17379 | 0.132 | 0.132 | 0.17379 | 0.17379 | 0.132 | 0.132 | 0.17379
|  | kW/m3/hr | C2 | 0.1767 | 0.132 | 0.132 | 0.21107 | 0.17458 | 0.132 | 0.132 | 0.17458 | 0.1767 | 0.132 | 0.132 | 0.1767 | 0.18776 | 0.132 | 0.132 | 0.18776 | 0.18776 | 0.132 | 0.132 | 0.18776
|  | kW/m3/hr | C3 | 0.31122 | 0.132 | 0.132 | 0.29945 | 0.17795 | 0.132 | 0.132 | 0.17795 | 0.19676 | 0.132 | 0.132 | 0.19676 | 0.23151 | 0.132 | 0.132 | 0.23151 | 0.23151 | 0.132 | 0.132 | 0.23151
|  | kW/m3/hr | C4 | 0.20778 | 0.13348 | 0.13348 | 0.25968 | 0.43855 | 0.13348 | 0.13348 | 0.43855 | 0.17799 | 0.13348 | 0.13348 | 0.17799 | 0.85279 | 0.13348 | 0.13348 | 0.85279 | 0.85279 | 0.13348 | 0.13348 | 0.85279
|  | kW/m3/hr | C5 | 0.14601 | 0.14675 | 0.04397 | 0.044488 | 0.14747 | 0.14747 | 0.6567 | 0.6567 | 0.14747 | 0.14747 | 0.50829 | 0.50829 | 0.14747 | 0.14747 | 0.67348 | 0.67348 | 0.14747 | 0.14747 | 0.67348 | 0.67348
|  | kW/m3/hr | C6 | 0.23306 | 0.14406 | 0.14406 | 11.2923 | 0.25267 | 0.14406 | 0.14406 | 0.25267 | 0.92035 | 0.14406 | 0.14406 | 0.92035 | 0.19059 | 0.14406 | 0.14406 | 0.19059 | 0.19059 | 0.14406 | 0.14406 | 0.19059
|  | kW/m3/hr | Total | 0.20531 | 0.13568 | 0.091009 | 0.18661 | 0.20924 | 0.13714 | 0.20773 | 0.27983 | 0.21184 | 0.13582 | 0.20183 | 0.27786 | 0.20966 | 0.13854 | 0.20951 | 0.28063 | 0.20966 | 0.13854 | 0.20951 | 0.28063
| Time Loaded | hrs | C1 | 5120 | 5120 | 4604 | 4619 | 5204 | 5204 | 5204 | 5204 | 5120 | 5120 | 5120 | 5120 | 5055 | 5055 | 5055 | 5055 | 5055 | 5055 | 5055 | 5055
|  | hrs | C2 | 4922 | 4922 | 3737 | 3756 | 5018 | 5018 | 5018 | 5018 | 4922 | 4922 | 4922 | 4922 | 4475 | 4475 | 4475 | 4475 | 4475 | 4475 | 4475 | 4475
|  | hrs | C3 | 2222 | 4166 | 1323 | 2334 | 4867 | 4867 | 4867 | 4867 | 4167 | 4167 | 4167 | 4167 | 3292 | 3292 | 3292 | 3292 | 3292 | 3292 | 3292 | 3292
|  | hrs | C4 | 3907 | 4955 | 1811 | 2856 | 1482 | 1482 | 1482 | 1482 | 4953 | 4953 | 4953 | 4953 | 701 | 701 | 701 | 701 | 701 | 701 | 701 | 701
|  | hrs | C5 | 6720 | 6755 | 6742 | 6766 | 6816 | 6816 | 8256 | 8256 | 6816 | 6816 | 8256 | 8256 | 6816 | 6816 | 8256 | 8256 | 6816 | 6816 | 8256 | 8256
|  | hrs | C6 | 3693 | 701 | 1098 | 53 | 3292 | 3292 | 3292 | 3292 | 701 | 701 | 701 | 701 | 5016 | 5016 | 5016 | 5016 | 5016 | 5016 | 5016 | 5016
|  | hrs | Total | 26584 | 26619 | 19315 | 20384 | 26679 | 26679 | 28119 | 28119 | 26679 | 26679 | 28119 | 28119 | 25355 | 25355 | 26795 | 26795 | 25355 | 25355 | 26795 | 26795
| Time Loaded | % | C1 | 62.02% | 62.02% | 55.77% | 55.95% | 63.03% | 63.03% | 63.03% | 63.03% | 62.02% | 62.02% | 62.02% | 62.02% | 61.23% | 61.23% | 61.23% | 61.23% | 61.23% | 61.23% | 61.23% | 61.23%
|  | % | C2 | 59.62% | 59.62% | 45.26% | 45.49% | 60.78% | 60.78% | 60.78% | 60.78% | 59.62% | 59.62% | 59.62% | 59.62% | 54.2% | 54.2% | 54.2% | 54.2% | 54.2% | 54.2% | 54.2% | 54.2%
|  | % | C3 | 26.91% | 50.46% | 16.02% | 28.27% | 58.95% | 58.95% | 58.95% | 58.95% | 50.47% | 50.47% | 50.47% | 50.47% | 39.87% | 39.87% | 39.87% | 39.87% | 39.87% | 39.87% | 39.87% | 39.87%
|  | % | C4 | 47.32% | 60.02% | 21.94% | 34.59% | 17.95% | 17.95% | 17.95% | 17.95% | 59.99% | 59.99% | 59.99% | 59.99% | 8.491% | 8.491% | 8.491% | 8.491% | 8.491% | 8.491% | 8.491% | 8.491%
|  | % | C5 | 81.4% | 81.82% | 81.66% | 81.95% | 82.56% | 82.56% | 100% | 100% | 82.56% | 82.56% | 100% | 100% | 82.56% | 82.56% | 100% | 100% | 82.56% | 82.56% | 100% | 100%
|  | % | C6 | 44.73% | 8.491% | 13.3% | 0.642% | 39.87% | 39.87% | 39.87% | 39.87% | 8.491% | 8.491% | 8.491% | 8.491% | 60.76% | 60.76% | 60.76% | 60.76% | 60.76% | 60.76% | 60.76% | 60.76%
|  | % | Total | 53.67% | 53.74% | 38.99% | 41.15% | 53.86% | 53.86% | 56.76% | 56.76% | 53.86% | 53.86% | 56.76% | 56.76% | 51.18% | 51.18% | 54.09% | 54.09% | 51.18% | 51.18% | 54.09% | 54.09%
| Time Unloaded | hrs | C1 | 3136 | 3136 | 3652 | 3637 | 3052 | 3052 | 3052 | 3052 | 3136 | 3136 | 3136 | 3136 | 3201 | 3201 | 3201 | 3201 | 3201 | 3201 | 3201 | 3201
|  | hrs | C2 | 3334 | 3334 | 4519 | 4500 | 3238 | 3238 | 3238 | 3238 | 3334 | 3334 | 3334 | 3334 | 3781 | 3781 | 3781 | 3781 | 3781 | 3781 | 3781 | 3781
|  | hrs | C3 | 6034 | 4090 | 6933 | 5922 | 3389 | 3389 | 3389 | 3389 | 4089 | 4089 | 4089 | 4089 | 4964 | 4964 | 4964 | 4964 | 4964 | 4964 | 4964 | 4964
|  | hrs | C4 | 4349 | 3301 | 6445 | 5400 | 6774 | 6774 | 6774 | 6774 | 3303 | 3303 | 3303 | 3303 | 7555 | 7555 | 7555 | 7555 | 7555 | 7555 | 7555 | 7555
|  | hrs | C5 | 1536 | 1501 | 1514 | 1490 | 1440 | 1440 | 0 | 0 | 1440 | 1440 | 0 | 0 | 1440 | 1440 | 0 | 0 | 1440 | 1440 | 0 | 0
|  | hrs | C6 | 4563 | 7555 | 7158 | 8203 | 4964 | 4964 | 4964 | 4964 | 7555 | 7555 | 7555 | 7555 | 3240 | 3240 | 3240 | 3240 | 3240 | 3240 | 3240 | 3240
|  | hrs | Total | 22952 | 22917 | 30221 | 29152 | 22857 | 22857 | 21417 | 21417 | 22857 | 22857 | 21417 | 21417 | 24181 | 24181 | 22741 | 22741 | 24181 | 24181 | 22741 | 22741
| Time Unloaded | % | C1 | 37.98% | 37.98% | 44.23% | 44.05% | 36.97% | 36.97% | 36.97% | 36.97% | 37.98% | 37.98% | 37.98% | 37.98% | 38.77% | 38.77% | 38.77% | 38.77% | 38.77% | 38.77% | 38.77% | 38.77%
|  | % | C2 | 40.38% | 40.38% | 54.74% | 54.51% | 39.22% | 39.22% | 39.22% | 39.22% | 40.38% | 40.38% | 40.38% | 40.38% | 45.8% | 45.8% | 45.8% | 45.8% | 45.8% | 45.8% | 45.8% | 45.8%
|  | % | C3 | 73.09% | 49.54% | 83.98% | 71.73% | 41.05% | 41.05% | 41.05% | 41.05% | 49.53% | 49.53% | 49.53% | 49.53% | 60.13% | 60.13% | 60.13% | 60.13% | 60.13% | 60.13% | 60.13% | 60.13%
|  | % | C4 | 52.68% | 39.98% | 78.06% | 65.41% | 82.05% | 82.05% | 82.05% | 82.05% | 40.01% | 40.01% | 40.01% | 40.01% | 91.51% | 91.51% | 91.51% | 91.51% | 91.51% | 91.51% | 91.51% | 91.51%
|  | % | C5 | 18.6% | 18.18% | 18.34% | 18.05% | 17.44% | 17.44% | 0% | 0% | 17.44% | 17.44% | 0% | 0% | 17.44% | 17.44% | 0% | 0% | 17.44% | 17.44% | 0% | 0%
|  | % | C6 | 55.27% | 91.51% | 86.7% | 99.36% | 60.13% | 60.13% | 60.13% | 60.13% | 91.51% | 91.51% | 91.51% | 91.51% | 39.24% | 39.24% | 39.24% | 39.24% | 39.24% | 39.24% | 39.24% | 39.24%
|  | % | Total | 46.33% | 46.26% | 61.01% | 58.85% | 46.14% | 46.14% | 43.24% | 43.24% | 46.14% | 46.14% | 43.24% | 43.24% | 48.82% | 48.82% | 45.91% | 45.91% | 48.82% | 48.82% | 45.91% | 45.91%
| Total Time | hrs | C1 | 8256 | 8256 | 8256 | 8256 | 8256 | 8256 | 8256 | 8256 | 8256 | 8256 | 8256 | 8256 | 8256 | 8256 | 8256 | 8256 | 8256 | 8256 | 8256 | 8256
|  | hrs | C2 | 8256 | 8256 | 8256 | 8256 | 8256 | 8256 | 8256 | 8256 | 8256 | 8256 | 8256 | 8256 | 8256 | 8256 | 8256 | 8256 | 8256 | 8256 | 8256 | 8256
|  | hrs | C3 | 8256 | 8256 | 8256 | 8256 | 8256 | 8256 | 8256 | 8256 | 8256 | 8256 | 8256 | 8256 | 8256 | 8256 | 8256 | 8256 | 8256 | 8256 | 8256 | 8256
|  | hrs | C4 | 8256 | 8256 | 8256 | 8256 | 8256 | 8256 | 8256 | 8256 | 8256 | 8256 | 8256 | 8256 | 8256 | 8256 | 8256 | 8256 | 8256 | 8256 | 8256 | 8256
|  | hrs | C5 | 8256 | 8256 | 8256 | 8256 | 8256 | 8256 | 8256 | 8256 | 8256 | 8256 | 8256 | 8256 | 8256 | 8256 | 8256 | 8256 | 8256 | 8256 | 8256 | 8256
|  | hrs | C6 | 8256 | 8256 | 8256 | 8256 | 8256 | 8256 | 8256 | 8256 | 8256 | 8256 | 8256 | 8256 | 8256 | 8256 | 8256 | 8256 | 8256 | 8256 | 8256 | 8256
|  | hrs | Total | 49536 | 49536 | 49536 | 49536 | 49536 | 49536 | 49536 | 49536 | 49536 | 49536 | 49536 | 49536 | 49536 | 49536 | 49536 | 49536 | 49536 | 49536 | 49536 | 49536
| Loaded Energy | kWh | C1 | 836000 | 640000 | 575500 | 804687.5 | 841250 | 650500 | 650500 | 841250 | 836000 | 640000 | 640000 | 836000 | 831937.5 | 631875 | 631875 | 831937.5 | 831937.5 | 631875 | 631875 | 831937.5
|  | kWh | C2 | 823625 | 615250 | 467125 | 750750 | 829625 | 627250 | 627250 | 829625 | 823625 | 615250 | 615250 | 823625 | 795687.5 | 559375 | 559375 | 795687.5 | 795687.5 | 559375 | 559375 | 795687.5
|  | kWh | C3 | 654875 | 520750 | 165375 | 661875 | 820187.5 | 608375 | 608375 | 820187.5 | 776437.5 | 520875 | 520875 | 776437.5 | 721750 | 411500 | 411500 | 721750 | 721750 | 411500 | 411500 | 721750
|  | kWh | C4 | 1076425.5 | 877035 | 320547 | 983412 | 861813 | 262314 | 262314 | 861813 | 1168996.5 | 876681 | 876681 | 1168996.5 | 792694.5 | 124077 | 124077 | 792694.5 | 792694.5 | 124077 | 124077 | 792694.5
|  | kWh | C5 | 338815 | 701564 | 549516 | 538751.2 | 534328.7742 | 534328.7742 | 2379511.4323 | 2379511.4323 | 705225.8802 | 705225.8802 | 2430780.5641 | 2430780.5641 | 520084.6452 | 520084.6452 | 2375238.1935 | 2375238.1935 | 520084.6452 | 520084.6452 | 2375238.1935 | 2375238.1935
|  | kWh | C6 | 1011882 | 192074 | 300852 | 14522 | 902008 | 902008 | 902008 | 902008 | 192074 | 192074 | 192074 | 192074 | 1374384 | 1374384 | 1374384 | 1374384 | 1374384 | 1374384 | 1374384 | 1374384
|  | kWh | Total | 4741622.5 | 3546673 | 2378915 | 3753997.7 | 4789212.2742 | 3584775.7742 | 5429958.4323 | 6634394.9323 | 4502358.8802 | 3550105.8802 | 5275660.5641 | 6227913.5641 | 5036538.1452 | 3621295.6452 | 5476449.1935 | 6891691.6935 | 5036538.1452 | 3621295.6452 | 5476449.1935 | 6891691.6935
| Loaded Energy | % | C1 | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100%
|  | % | C2 | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100%
|  | % | C3 | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100%
|  | % | C4 | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100%
|  | % | C5 | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100%
|  | % | C6 | 61.81% | 100% | 100% | 1.276% | 57.01% | 100% | 100% | 57.01% | 15.65% | 100% | 100% | 15.65% | 75.59% | 100% | 100% | 75.59% | 75.59% | 100% | 100% | 75.59%
|  | % | Total | 88.35% | 100% | 100% | 76.96% | 87.57% | 100% | 100% | 90.7% | 81.31% | 100% | 100% | 85.75% | 91.9% | 100% | 100% | 93.95% | 91.9% | 100% | 100% | 93.95%
| Unloaded Energy | kWh | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | kWh | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | kWh | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | kWh | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | kWh | C5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | kWh | C6 | 625131 | 0 | 0 | 1123811 | 680068 | 0 | 0 | 680068 | 1035035 | 0 | 0 | 1035035 | 443880 | 0 | 0 | 443880 | 443880 | 0 | 0 | 443880
|  | kWh | Total | 625131 | 0 | 0 | 1123811 | 680068 | 0 | 0 | 680068 | 1035035 | 0 | 0 | 1035035 | 443880 | 0 | 0 | 443880 | 443880 | 0 | 0 | 443880
| Unloaded Energy | % | C1 | bar: Opt op1 to CS4 op4
|  | % | C2 | bar: Opt op1 to CS4 op4
|  | % | C3 | bar: Opt op1 to CS4 op4
|  | % | C4 | bar: Opt op1 to CS4 op4
|  | % | C5 | bar: Opt op1 to CS4 op4
|  | % | C6 | 38.19% | 0% | 0% | 98.72% | 42.99% | 0% | 0% | 42.99% | 84.35% | 0% | 0% | 84.35% | 24.41% | 0% | 0% | 24.41% | 24.41% | 0% | 0% | 24.41%
|  | % | Total | 11.65% | 0% | 0% | 23.04% | 12.43% | 0% | 0% | 9.298% | 18.69% | 0% | 0% | 14.25% | 8.099% | 0% | 0% | 6.051% | 8.099% | 0% | 0% | 6.051%
| Total Energy | kWh | C1 | 836000 | 640000 | 575500 | 804687.5 | 841250 | 650500 | 650500 | 841250 | 836000 | 640000 | 640000 | 836000 | 831937.5 | 631875 | 631875 | 831937.5 | 831937.5 | 631875 | 631875 | 831937.5
|  | kWh | C2 | 823625 | 615250 | 467125 | 750750 | 829625 | 627250 | 627250 | 829625 | 823625 | 615250 | 615250 | 823625 | 795687.5 | 559375 | 559375 | 795687.5 | 795687.5 | 559375 | 559375 | 795687.5
|  | kWh | C3 | 654875 | 520750 | 165375 | 661875 | 820187.5 | 608375 | 608375 | 820187.5 | 776437.5 | 520875 | 520875 | 776437.5 | 721750 | 411500 | 411500 | 721750 | 721750 | 411500 | 411500 | 721750
|  | kWh | C4 | 1076425.5 | 877035 | 320547 | 983412 | 861813 | 262314 | 262314 | 861813 | 1168996.5 | 876681 | 876681 | 1168996.5 | 792694.5 | 124077 | 124077 | 792694.5 | 792694.5 | 124077 | 124077 | 792694.5
|  | kWh | C5 | 338815 | 701564 | 549516 | 538751.2 | 534328.7742 | 534328.7742 | 2379511.4323 | 2379511.4323 | 705225.8802 | 705225.8802 | 2430780.5641 | 2430780.5641 | 520084.6452 | 520084.6452 | 2375238.1935 | 2375238.1935 | 520084.6452 | 520084.6452 | 2375238.1935 | 2375238.1935
|  | kWh | C6 | 1637013 | 192074 | 300852 | 1138333 | 1582076 | 902008 | 902008 | 1582076 | 1227109 | 192074 | 192074 | 1227109 | 1818264 | 1374384 | 1374384 | 1818264 | 1818264 | 1374384 | 1374384 | 1818264
|  | kWh | Total | 5366753.5 | 3546673 | 2378915 | 4877808.7 | 5469280.2742 | 3584775.7742 | 5429958.4323 | 7314462.9323 | 5537393.8802 | 3550105.8802 | 5275660.5641 | 7262948.5641 | 5480418.1452 | 3621295.6452 | 5476449.1935 | 7335571.6935 | 5480418.1452 | 3621295.6452 | 5476449.1935 | 7335571.6935
| Loaded Cost | £ | C1 | 75960.8323 | 58151.8334 | 52291.2189 | 73115.7085 | 76437.8591 | 59105.8869 | 59105.8869 | 76437.8591 | 75960.8323 | 58151.8334 | 58151.8334 | 75960.8323 | 75591.7045 | 57413.5777 | 57413.5777 | 75591.7045 | 75591.7045 | 57413.5777 | 57413.5777 | 75591.7045
|  | £ | C2 | 74836.4121 | 55902.9929 | 42444.0237 | 68214.8264 | 75381.5856 | 56993.3398 | 56993.3398 | 75381.5856 | 74836.4121 | 55902.9929 | 55902.9929 | 74836.4121 | 72297.9483 | 50826.0653 | 50826.0653 | 72297.9483 | 72297.9483 | 50826.0653 | 50826.0653 | 72297.9483
|  | £ | C3 | 59503.4092 | 47316.5113 | 15026.3429 | 60139.4449 | 74524.0732 | 55278.315 | 55278.315 | 74524.0732 | 70548.8502 | 47327.8691 | 47327.8691 | 70548.8502 | 65579.8215 | 37389.8116 | 37389.8116 | 65579.8215 | 65579.8215 | 37389.8116 | 37389.8116 | 65579.8215
|  | £ | C4 | 97806.4317 | 79689.3643 | 29125.6183 | 89355.0168 | 78306.2593 | 23834.4375 | 23834.4375 | 78306.2593 | 106217.6401 | 79657.1991 | 79657.1991 | 106217.6401 | 72025.9976 | 11273.9141 | 11273.9141 | 72025.9976 | 72025.9976 | 11273.9141 | 11273.9141 | 72025.9976
|  | £ | C5 | 30785.4897 | 63745.6763 | 49930.2545 | 48952.1406 | 48550.3091 | 48550.3091 | 216207.738 | 216207.738 | 64078.4029 | 64078.4029 | 220866.1661 | 220866.1661 | 47256.0557 | 47256.0557 | 215819.462 | 215819.462 | 47256.0557 | 47256.0557 | 215819.462 | 215819.462
|  | £ | C6 | 91941.8648 | 17452.2738 | 27336.0865 | 1319.5014 | 81958.4671 | 81958.4671 | 81958.4671 | 81958.4671 | 17452.2738 | 17452.2738 | 17452.2738 | 17452.2738 | 124879.6084 | 124879.6084 | 124879.6084 | 124879.6084 | 124879.6084 | 124879.6084 | 124879.6084 | 124879.6084
|  | £ | Total | 430834.4399 | 322258.6521 | 216153.5448 | 341096.6387 | 435158.5534 | 325720.7555 | 493378.1844 | 602815.9823 | 409094.4116 | 322570.5713 | 479358.3345 | 565882.1748 | 457631.1359 | 329039.0327 | 497602.439 | 626194.5422 | 457631.1359 | 329039.0327 | 497602.439 | 626194.5422
| Unloaded Cost | £ | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | £ | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | £ | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | £ | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | £ | C5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | £ | C6 | 56800.8027 | 0 | 0 | 102111.9844 | 61792.5016 | 0 | 0 | 61792.5016 | 94045.5982 | 0 | 0 | 94045.5982 | 40331.9309 | 0 | 0 | 40331.9309 | 40331.9309 | 0 | 0 | 40331.9309
|  | £ | Total | 56800.8027 | 0 | 0 | 102111.9844 | 61792.5016 | 0 | 0 | 61792.5016 | 94045.5982 | 0 | 0 | 94045.5982 | 40331.9309 | 0 | 0 | 40331.9309 | 40331.9309 | 0 | 0 | 40331.9309
| Total Cost | £ | C1 | 75960.8323 | 58151.8334 | 52291.2189 | 73115.7085 | 76437.8591 | 59105.8869 | 59105.8869 | 76437.8591 | 75960.8323 | 58151.8334 | 58151.8334 | 75960.8323 | 75591.7045 | 58151.8334 | 57413.5777 | 75591.7045 | 75591.7045 | 58151.8334 | 57413.5777 | 75591.7045
|  | £ | C2 | 74836.4121 | 55902.9929 | 42444.0237 | 68214.8264 | 75381.5856 | 56993.3398 | 56993.3398 | 75381.5856 | 74836.4121 | 55902.9929 | 55902.9929 | 74836.4121 | 72297.9483 | 55902.9929 | 50826.0653 | 72297.9483 | 72297.9483 | 55902.9929 | 50826.0653 | 72297.9483
|  | £ | C3 | 59503.4092 | 47316.5113 | 15026.3429 | 60139.4449 | 74524.0732 | 55278.315 | 55278.315 | 74524.0732 | 70548.8502 | 47327.8691 | 47327.8691 | 70548.8502 | 65579.8215 | 47327.8691 | 37389.8116 | 65579.8215 | 65579.8215 | 47327.8691 | 37389.8116 | 65579.8215
|  | £ | C4 | 97806.4317 | 79689.3643 | 29125.6183 | 89355.0168 | 78306.2593 | 23834.4375 | 23834.4375 | 78306.2593 | 106217.6401 | 79657.1991 | 79657.1991 | 106217.6401 | 72025.9976 | 79657.1991 | 11273.9141 | 72025.9976 | 72025.9976 | 79657.1991 | 11273.9141 | 72025.9976
|  | £ | C5 | 30785.4897 | 63745.6763 | 49930.2545 | 48952.1406 | 48550.3091 | 48550.3091 | 216207.738 | 216207.738 | 64078.4029 | 64078.4029 | 220866.1661 | 220866.1661 | 47256.0557 | 64078.4029 | 215819.462 | 215819.462 | 47256.0557 | 64078.4029 | 215819.462 | 215819.462
|  | £ | C6 | 148742.6675 | 17452.2738 | 27336.0865 | 103431.4858 | 143750.9687 | 81958.4671 | 81958.4671 | 143750.9687 | 111497.872 | 17452.2738 | 17452.2738 | 111497.872 | 165211.5393 | 17452.2738 | 124879.6084 | 165211.5393 | 165211.5393 | 17452.2738 | 124879.6084 | 165211.5393
|  | £ | Total | 487635.2426 | 322258.6521 | 216153.5448 | 443208.6231 | 496951.055 | 325720.7555 | 493378.1844 | 664608.4838 | 503140.0098 | 322570.5713 | 479358.3345 | 659927.773 | 497963.0669 | 322570.5713 | 497602.439 | 666526.4732 | 497963.0669 | 322570.5713 | 497602.439 | 666526.4732

## Average Efficiency
|  |  | Opt |  |  |  | CS1 |  |  |  | CS2 |  |  |  | CS3 |  |  |  | CS4
|  | Units | op1 | op2 | op3 | op4 | op1 | op2 | op3 | op4 | op1 | op2 | op3 | op4 | op1 | op2 | op3 | op4 | op1 | op2 | op3 | op4
Average Efficiency | C1 | kW/m3/hr | 0.17242 | 0.132 | 0.132 | 0.18396 | 0.1707 | 0.132 | 0.132 | 0.1707 | 0.17242 | 0.132 | 0.132 | 0.17242 | 0.17379 | 0.132 | 0.132 | 0.17379 | 0.17379 | 0.132 | 0.132 | 0.17379
| C2 | kW/m3/hr | 0.1767 | 0.132 | 0.132 | 0.21107 | 0.17458 | 0.132 | 0.132 | 0.17458 | 0.1767 | 0.132 | 0.132 | 0.1767 | 0.18776 | 0.132 | 0.132 | 0.18776 | 0.18776 | 0.132 | 0.132 | 0.18776
| C3 | kW/m3/hr | 0.31122 | 0.132 | 0.132 | 0.29945 | 0.17795 | 0.132 | 0.132 | 0.17795 | 0.19676 | 0.132 | 0.132 | 0.19676 | 0.23151 | 0.132 | 0.132 | 0.23151 | 0.23151 | 0.132 | 0.132 | 0.23151
| C4 | kW/m3/hr | 0.20778 | 0.13348 | 0.13348 | 0.25968 | 0.43855 | 0.13348 | 0.13348 | 0.43855 | 0.17799 | 0.13348 | 0.13348 | 0.17799 | 0.85279 | 0.13348 | 0.13348 | 0.85279 | 0.85279 | 0.13348 | 0.13348 | 0.85279
| C5 | kW/m3/hr | 0.14601 | 0.14675 | 0.04397 | 0.044488 | 0.14747 | 0.14747 | 0.6567 | 0.6567 | 0.14747 | 0.14747 | 0.50829 | 0.50829 | 0.14747 | 0.14747 | 0.67348 | 0.67348 | 0.14747 | 0.14747 | 0.67348 | 0.67348
| C6 | kW/m3/hr | 0.23306 | 0.14406 | 0.14406 | 11.2923 | 0.25267 | 0.14406 | 0.14406 | 0.25267 | 0.92035 | 0.14406 | 0.14406 | 0.92035 | 0.19059 | 0.14406 | 0.14406 | 0.19059 | 0.19059 | 0.14406 | 0.14406 | 0.19059